## GRAND SUMMARY
PROJECT: CONSTRUCTION OF CENTRAL WAREHOUSE, PT PANEL PRODUCTION AND BIO-BANK
CLIENT:MINSTRY OF HEALTH
CONSULTANT:MINISTRY OF HEALTH - Health Infrastructure Lead Executive Officer
CONTRACTOR-
LOCATION : ADDIS ABABA
GRAND SUMMARY OF BILL OF QUANTITIES
IN | DESCRIPTION
1 | WAREHOUSE, STORE & PT PRODUCTION BUILDING | 0
2 | SITE WORK & LANDESCAPING | 0
TOTAL |  | 0
15% VAT |  | 0
GRAND TOTAL INCLUDING 15% VAT |  | 0

## Main Building SUMMARY
SUMMARY
OF
BILL OF QUANTITIES
FOR
THE CONSTRUCTION OF CENTRAL WAREHOUSE, PT PANEL PRODUCTION AND BIO-BANK BUILDING
MAIN BUILDING
IN | DESCRIPTION
A-SUB STRUCTURE |  |  | AMOUNT
1 | EXCAVATION AND EARTH WORK................................................................................. | Birr | 0
2 | CONCRETE WORK...................................................................................................... | Birr | 0
3 | MASONARY WORK................................................................................................... | Birr | 0
| TOTAL A........... | Birr | 0
B. SUPER STRUCTURE
1 | CONCRETE WORK...................................................................................................... | Birr | 0
2 | BLOCK WORK.................................................................................................................. | Birr | 0
3 | ROOFING & STEEL STRUCTURE................................................................................................................. | Birr | 0
4 | CARPENTARY AND JOINERY............................................................................... | Birr | 0
5 | ALUMINIUM WORK............................................................ | Birr | 0
6 | PLASTERING WORK ............................................................................................................. | Birr | 0
7 | FINISHING WORK............................................................................................................... | Birr | 0
8 | PAINTING WORK................................................................................................................. | Birr | 0
9 | SANITARY INSTALLATION……………………………………………………………………. | Birr | 0
10 | ELECTRICAL INSTALLATION ……………………………………………………………………. | Birr | 0
11 | DATA SYSTEM WORKS ……………………………………………………………………. | Birr | 0
12 | ELECTRO MECHANICAL WORKS ……………………………………………………………………. | Birr | 0
| Total B ………......... | Birr | 0
| Total A + B ................... | Birr | 0

## BoQ for sub stru
Item No | Description | Unit | Quantity | Rate | Amount
A-SUB STRUCTURE
1. EXCAVATION & EARTH WORK
1.1 | General site clearance, including the removal of any accumulated rubbish, debris, and unwanted vegetation to prepare the site for restarting construction activities. Preparation and levelling of designated areas to create a safe, clean, and comfortable working space for site personnel and operations. This includes basic surface preparation as required. price shall include all removal of the unwanted materials & stock pile the scrap materials at designated location within the site boundaries as indicated by the Engineer/Site Supervisor. | lum | 1 |  | 0
1.2 | Fill under hard core with imported selected material from quarry waste well rolled and compacted in layers not exceeding 200 mm thick. | m3 | 1456 |  | 0
1.3 | 250mm thick basaltic stone hardcore well rolled, consolidated and blinded with crushed stone . | m2 | 122 |  | 0
| Total carried to Summary |  |  |  | 0
2. CONCRETE WORK
2.01 | 50 mm lean concrete quality C-5, with minimum cement content of 150 kg /m3, of concrete: Under
| a) Masonry | m2 | 494.74 |  | 0
2.02 | Reinforced concrete quality C-30/37 ,420 kg of cement/m3 with Truck Mixer have minimum 28 day Cubic crushing strength of 37MP, filled in to form work and vibrated around rod reinforcement (formwork and reinforcement measured separately) |  |  |  | 0
| a) Lift shaft ,shear wall and Retaining wall | m3 | 458 |  | 0
2.03 | Reinforced concrete quality C-30 ,420 kg of cement/m3 with Truck Mixer have minimum 28 day Cubic Crushing strength of 37MP, filled in to form work and vibrated around rod reinforcement (formwork and reinforcement measured separately) |  |  |  | 0
| a) In 2nd Basement Floor slab | m3 | 531 |  | 0
| c) In 2nd Basement Floor beams | m3 | 7.5974 |  | 0
| d) In 19mm thick 1st Basement Floor slab | m3 | 269.9325 |  | 0
| e) In 1st Basement Floor beams | m3 | 53.2259 |  | 0
| f) In Ground Floor beams | m3 | 151.76 |  | 0
| g) In 19 cm thick ground floor slab | m3 | 584.45 |  | 0
| h) Shear wall | m3 | 224 |  | 0
| i) In Entrance Staircase | m3 | 6.0639 |  | 0
| j) In Stair case | m3 | 33 |  | 0
| k) In Ramp | m3 | 288.2 |  | 0
2.04 | Reinforced concrete quality C-40 ,504 kg of cement/m3 with Truck Mixer have minimum 28 day Cubic crushing strength of 40MP, filled in to form work and vibrated around rod reinforcement (formwork and reinforcement measured separately) |  |  |  | 0
| a) In Foundation column | m3 | 128.4255 |  | 0
| Shoring and Related Works (Design and build) |  |  |  | 0
2.05 | Rehabilitation of the existing Soil Protection Works: All activities necessary to restore the functionality and integrity of the existing soil protection measures to the required standards and specifications. This may involve repair, replacement, or enhancement of components. Reinstatement of Existing Piles: All activities required to repair, strengthen, or otherwise reinstate the existing piles to ensure they meet the specified structural and load-bearing requirements. Associated Works: Any ancillary or incidental works required to facilitate, complete, and integrate the soil protection rehabilitation and pile reinstatement, ensuring a fully functional and durable system as per the project design and specifications. N:B Site Visit is required | Ls | 1 |  | 0
2.06 | Provide, fabricate and erect water proof well bonded plywood or water tight fiberboard or hard board. Forms shall be tied and braced with standard tie spacing horizontally and vertically so that the formwork resist concrete pressure to have true edge and shape of concrete surface. Forms shall be lined with water tight plastic to prevent mortar leakage. Props used for bracing and support of horizontal structures shall be adjustable steel. |  |  |  | 0
| a) In 2nd Basement Floor beams | m2 | 169.766 |  | 0
| c) In 19mm thick 1st Basement Floor slab | m2 | 1631.6364 |  | 0
| d) In 1st Basement Floor beams | m2 | 243.6748 |  | 0
| e) In Ground Floor beams | m2 | 971 |  | 0
| f) In 19 cm thick ground floor slab | m2 | 2583.33 |  | 0
| g) Lift shaft ,shear wall and Retaining wall | m2 | 126.2495 |  | 0
| h) In Entrance Staircase | m2 | 57.568 |  | 0
| i) In Stair case | m2 | 155.1295 |  | 0
| j) In Foundation column | m2 | 654.93 |  | 0
| k) In Ramp | m2 | 441 |  | 0
2.07 | Mild steel reinforcement according to structural drawings. Price includes cutting, bending, placing in position and tying wire. |  |  |  | 0
| a) Dia 8 mm deformed bar | kg | 6900 |  | 0
| b) Dia 10 mm deformed bar | kg | 295568.2341 |  | 0
| c) Dia 12 mm deformed bar | kg | 28714.3387 |  | 0
| d) Dia 14 mm deformed bar | kg | 47237.5695 |  | 0
| e) Dia 16 mm deformed bar | kg | 40114.3389 |  | 0
| f) Dia 20 mm deformed bar | kg | 39818.8862 |  | 0
| g) Dia 24 mm deformed bar | kg | 14600 |  | 0
| Total carried to Summary |  |  |  | 0
3.01 | 500mm thick hard trachytic or equivalent roughly dressed stone masonry wall below ground level bedded in cement mortar mix ratio (1:3). | m3 | 195 |  | 0
3.02 | Ditto but for exposed part above natural ground level. | m3 | 240 |  | 0
3.03 | Ditto but for retaining wall as per the detail drawing. | m3 | 512 |  | 0
| Total carried to Summary |  |  |  | 0
B-SUPER STRUCTURE
1. CONCRETE WORK
1.01 | Reinforced concrete quality C-25 ,360 kg of cement/m3 have minimum 28 day Cubic crushing strength of 25MPa filled in to form work and vibrated around rod reinforcement (formwork and reinforcement measured separately)
| a) Lift shaft and shear wall | m3 | 590 |  | 0
| b) Gutter and Parapet Concrete | m3 | 68 |  | 0
| c) lintels | m3 | 34 |  | 0
1.02 | Reinforced concrete quality C-30/37 ,420 kg of cement/m3 with Truck Mixer have minimum 28 day Cubic crushing strength of 30MPa filled in to form work and vibrated around rod reinforcement (formwork and reinforcement measured separately) |  |  |  | 0
| a) In floor beams | m3 | 968 |  | 0
| b) In 190mm thick Suspended Floor slab | m2 | 16402 |  | 0
| c) In 200mm thick Cantilever structures | m2 | 234 |  | 0
| d) In staircase and landing | m3 | 126 |  | 0
| e) In roof beams | m3 | 29.4 |  | 0
| f) In 190mm thick Roof slab and Water Tank Slab | m2 | 2568 |  | 0
1.03 | Reinforced concrete quality C-40 ,504kg of cement/m3 with Truck Mixer have minimum 28 day Cubic crushing strength of 40MP, filled in to form work and vibrated around rod reinforcement (formwork and reinforcement measured separately) |  |  |  | 0
| a) In elevation columns | m3 | 860 |  | 0
1.04 | Provide, fabricate and erect water proof well bonded plywood or water tight fiberboard or hard board. Forms shall be tied and braced with standard tie spacing horizontally and vertically so that the formwork resist concrete pressure to have true edge and shape of concrete surface. Forms shall be lined with water tight plastic to prevent mortar leakage. |  |  |  | 0
| a) Lift shaft and shear wall | m2 | 2121 |  | 0
0
| b) Gutter and Parapet Concrete | m2 | 304 |  | 0
0
| c) lintels | m2 | 151 |  | 0
0
| d) In elevation columns | m2 | 4222 |  | 0
0
| e) In floor beams | m2 | 4708 |  | 0
0
| f) In 190mm thick Suspended Floor slab | m2 | 16402 |  | 0
0
| g) In 200mm thick Cantilever structures | m2 | 234 |  | 0
0
| h) In staircase and landing | m2 | 696 |  | 0
0
| i) In roof beams | m2 | 196 |  | 0
0
| j) In 190mm thick Roof slab and Water Tank Slab | m2 | 2568 |  | 0
1.05 | Mild steel reinforcement according to structural drawings. Price includes cutting, bending, placing in position and tying wire. |  |  |  | 0
0
| a) Dia 8 mm deformed bar | kg | 1769 |  | 0
0
| b) Dia 10 mm deformed bar | kg | 686078.8 |  | 0
0
| c) Dia 12 mm deformed bar | kg | 481586.4 |  | 0
0
| d) Dia 14 mm deformed bar | kg | 2972 |  | 0
0
| e) Dia 16 mm deformed bar | kg | 215697.6 |  | 0
0
| f) Dia 20 mm deformed bar | kg | 218627 |  | 0
0
| g) Dia 24 mm deformed bar | kg | 11526 |  | 0
0
| Total carried to Summary |  |  |  | 0
2. BLOCK WORK
Attention to all bidders:
Application of coving (creating quarter circle) material is mandatory during block work construction. There are some clean rooms such as microbiology, reagent and related rooms where sharp corner or 90o is not recommended between wall to wall, wall to column, wall to floor and wall to ceiling. The item is stipulated under pay item 7.23 in Finishing Works and this is written as a reminder to bidders Coving is done parallel to HCB wall.
2.01 | 200mm thick hollow concrete block wall of type Class B, with 28 days minimum crushing strength of 32kg/cm2, bedded in cement mortar (1:3) mix, both sides left for plastering. | m2 | 6105 |  | 0
0
2.02 | Ditto but 2.01 but 150mm HCB. | m2 | 5638 |  | 0
0
2.03 | Ditto but 2.01 but 100mm HCB. | m2 | 870 |  | 0
0
2.04 | Ditto but 25 cm thick Brick wall both sides left for plastering; bedded in cement mortar (1:3). Price shall include mortar bed. | m2 | 755 |  | 0
0
2.05 | Ditto as item 2.04 but 12.5 cm thick Brick wall both sides left for plastering; bedded in cement mortar (1:3). Price shall include mortar bed. | m2 | 167 |  | 0
0
2.06 | Construction of Natural Stone wall cladding for exterior wall fitted to 200mm thick hollow concrete block wall that is similar in nature as main entrance of Ethiopian Public Health Institute (EPHI). Price Shall include cement:sand mortar (1:2) mix ratio and all related civil works. | m2 | 336 |  | 0
0
2.07 | Ditto as item 2.06 but Smooth finished stone Cladding | m2 | 1244 |  | 0
0
| Total carried to Summary |  |  |  | 0
3. ROOFING & STEEL STRUCTURE
3.01 | Average 120mm thick light weight concrete in mix(1:2:5) cement, pumice and sand laid over RC roof slab with 2% slope towards down pipe and corners angled at 45 degree at parapet and roof slab connection as shown on the drawing. Brush and blow out dirt,dust,latency,scrapings and all other loose material until the reinforced concrete slab is fully cleared. | m2 | 3250 |  | 0
0
3.02 | 50mm thick smooth finished cement sand screed laid on top of light weight concrete in Roof Slab and gutter in mortar mix (1:3) with proper slope towards down pipe. | m2 | 3250 |  | 0
0
3.03 | Supply and Apply APP modified , bitumen rich water proofing membrane or equvelent, thickness not les than 4mm. for concrete slab of the roof. The material shall conform to the quality requirements of BS or other equivalent institution. The construction shall be done by the supplier all in accordance with the manufacturers details and instruction and certified personnel. The cost shall include primecoats, cleaning of all dirt's, trace of grease, oil and loose particles. There shall be a minimum of 20 years guarantee. | m2 | 3250 |  | 0
0
3.04 | Apply cementious water proofing material on Concrete walls and columns as per the manufacturer's instruction. The cost shall include cleaning of all dirts, trace of grease, oil and loose particles. The work shall be done on subcontractual bases with the supplier of the material which will give material & construction gurantee to the client. | m2 | 2162.5 |  | 0
0
3.05 | Ditto but for the shear wall and lift Shaft core | m2 | 1060.5 |  | 0
0
3.06 | Supply and fix G-28 galvanized flat metal sheet flashing with development length of 1000mm as per the detail drawing. Price shall include all necessary accessories, metal brackets, one coat of antirust paint and two coat of synthetic enamel paint. | ml | 420 |  | 0
0
3.07 | Supply , assemble and fix DECRA or equivalent Roofing size as per manufacturer manual and instruction on purlin truss members Price shall includes 15cm wide ridge cap coverand & purlines all unstated works related to this item. | m2 | 520 |  | 0
3.08 | Supply and fix G-28 galvanised flat sheet metal Gutter as per the drawing. price shall include metal bracket support and all other necessary accessories. Development length = 1000mm. price shall include one coat of anti-rust and two coats of synthetic paint. | ml | 420 |  | 0
0
3.09 | Supply & fix 110mm diameter PVC down pipe secured to wall with metal bracket or strap with anchorage distance of 800mm. Price shall include PVC elbow, concrete support and all necessary accessories. | ml | 732.6 |  | 0
0
3.1 | STEEL STRUCTURE WORKS. |  |  |  | 0
| Supply & erect Steel members for roof structure all as per detail drawing. Price includes all necessary preparation works including one coat of antirust painting and all other necessary accessories |  |  |  | 0
| a) 60 x 50 x 3.2 mm RHS | kg | 8369.4 |  | 0
| b) 60 x 60 x 3.2 mm RHS | kg | 8935.5 |  | 0
| c) 80x40x3.2 mm RHS | kg | 9090.9 |  | 0
| d) 50x30x3.2 mm RHS | kg | 4365.63 |  | 0
| e) 30x30x3.2 mm RHS | kg | 7908.75 |  | 0
| f) 100x100x5 mm RHS | kg | 38770.08 |  | 0
| g) dia-16mm J anchor bolt length- 35 cm, 4pcs | No. | 704 |  | 0
| h) 2 plates (300 x 300 x 6mm) base plate | No. | 352 |  | 0
| i) 2 plates (450 x 280 x 6mm) Side plate | No. | 252 |  | 0
| j) 2 plates (460 x 190 x 6mm) Side plate | No. | 252 |  | 0
| k) 2 plates (140 x 150 x 6mm) connection plate | No. | 126 |  | 0
| l) angle - 40 x 25 x 25 x 4mm | No. | 1235 |  | 0
| m) Dia. 6mm Crank bolt | No. | 355 |  | 0
| n) Lattice purlin |  |  |  | 0
| n1 30x30x2.5 mm RHS | kg | 10080 |  | 0
| n2 25x25x2.5 mm RHS | kg | 4210 |  | 0
| n3 80x80x4.5 mm RHS | kg | 3255 |  | 0
| Total carried to Summary |  |  |  | 0
4. CARPENTRY AND JOINERY
4.01 | Supply and fix 40mm. thick flush wood door with hard wood frames and both sides covered with best quality 6mm. Thick MDF. Price includes approved quality lock, hinges, three coats of varnish paint, door stopper and all necessary accessories and shall comply with the Architectural Technical Specification Requirement and Engineer's approval.
0
| a ) D2 size:900x2100 mm. | No | 90 |  | 0
4.02 | Supply and fix Accustic Armstrong ceiling suspended on galvanized steel profiles. The steel profiles shall be of appropriate thickness and section suspended from steel truss according to the detail drawing and shall comply with the Architectural Technical Specification Requirement and Engineer's approval. | m² | 1624 |  | 0
0
4.03 | Supply and fix Aluminum board ceiling made of formed galvanized sheet metal trays with non-directional fissures and laid on pre-painted exposed T38 suspension system including Anodized aluminum frame with aluminum composite drop main and cross tees, hold-down clips, wedges, reinforcement splines, etc. Ceilings suspended with galvanized hangers at centers not exceeding 600mm below concrete soffits/truss and all ceilings must be installed as per specialist manufacturer Instructions. The price includes rectification works for any roof leakages. The size is 600 x 600 x Aluminum profile sheet (minimum 0.5mm thick) with complete framing. The price shall include suspension systems, the demolishing of the existing ceiling including the cart away, and all other necessary accessories. All work material quality, color, and application shall be approved by the Engineer. | m² | 4200 |  | 0
4.04 | Gypsum Ceiling: Supply and fix 8mm thick Gypsum board Ceiling where instructed by the Engineer according to design provided. The Ceiling shall be tightly secured and fixed with proper screw, fastener and fishers accordingly. The price shall include vertical and bend decoration boards, all sections and c-channel drywall metal frames both ways with anchor, gypsum chucking, Painting and all necessary materials for the work. The quality and colour shall be as per the client recommendation and approval.(Note: Bends not considered, measurement shall be taken only on X-Y horizontal projection direction) | m² | 2500 |  | 0
4.05 | Supply and Fix Decorative Cladding for Column, ceilings & walls with treated wood or green carbon wooden material (teak, cedar) as per the design, and Engineers approval for color and material. | m² | 355 |  | 0
4.06 | Gypsum Walling: Supply and fix 8mm thick double Gypsum board Partition wall. The wall is fixed to the floor, ceiling, beam, and column surface according to the detail drawing attached. The partition shall be tightly secured and fixed with proper screw, fastener, and fishers accordingly. The price shall include vertical and bend decoration boards, photo frame boards, all sections and c-channel dry wall metal frames both ways with anchor, gypsum chucking, and all necessary materials for the work. The quality and color shall be as per the client recommendation and approval. (Note: Bends not considered, measurement shall be taken only on vertical direction) | m² | 250 |  | 0
4.07 | Supply and install WPC for Wall and Columns Panels. Includes necessary mounting tracks, adhesive, and trim profiles with all accessories . | m² | 650 |  | 0
4.08 | Supply and install UV (High Gloss) Wall Panels. Includes necessary backing, bonding, and trim profiles for seamless installation. | m² | 850 |  | 0
| Total carried to Summary |  |  |  | 0
| 5. ALUMINIUM WORK |  |  |  | 0
0
5.01 | Doors and windows made of Aluminium tubular profile frames ALLCO-5 or equivalent ,1.6mm thick average weight 1000gm/ml,door kick plate 1500gm/ml,partly covered with aluminium sheet according to the detail drawing and window door schedule .Complete work includes all the necessary iron mongery and best quality cylinderical lock ,hinges ,rubber sealants , 6mm Brown tinted/figured glass for doors, 5mm clear glass for windows door stopper and fixing hard wares to make the door/window complete. All Aluminium windows and doors type shall comply with the Architectural Technical Specification Requirement and Engineer's approval. |  |  |  | 0
0
| WINDOWS |  |  |  | 0
0
| a)W1 Size 5000x2000 mm | No | 68 |  | 0
0
| b)W2 Size 4000x2000 mm | No | 17 |  | 0
0
| c)W3 Size 2500x2000 mm | No | 38 |  | 0
0
| d)W4 Size 2000x2000 mm | No | 45 |  | 0
0
| e)W5 Size 1600x2000 mm | No | 23 |  | 0
0
| f)W6 Size 1000x2000 mm | No | 53 |  | 0
0
| f)W7 Size 1000x1000 mm | No | 128 |  | 0
| TOP WINDOWS |  |  |  | 0
0
| a)TW1, Size 5000x1000 mm | No | 21 |  | 0
0
| b)TW2, Size 2500x1000 mm | No | 26 |  | 0
0
5.02 | ALUMINIUM LOUVER |  |  |  | 0
0
| Exterior Louvers shall be constructed entirely from extruded aluminum, alloy 6063-T5. Blades and frames shall be minimum 2.06 mm thickness. Louver height shall be 1000mm stationary, horizontal fixed to concrete with aluminium support hanger and fastner as per detail drawing. Louvers shall be supplied with a standard mill finish or the natural shiny appearance of the aluminium. Each louver shall be fitted with 12.7mm mesh and 1.6mm diameter aluminum bird screen all as per the given detail design. Manufacturer shall warrant the material of this Section for a period of 5 years from date of Substantial Completion against possible material defects. Installer shall also warrant the workmanship of this Section for a period of 2 years from date of Substantial Completion against defects in Workmanship. Color and pattern will be Approved by the Engineer. |  |  |  | 0
|  | m2 | 285 |  | 0
5.03 | DOORS |  |  |  | 0
| a) D1 Size 2000 x 3000 mm Self Closing | No | 17 |  | 0
| b) D2 size: 1600x3000 mm Self Closing | No | 16 |  | 0
| c) D3 size: 1600x3000 mm | No | 16 |  | 0
| d) D4 size: 1200x3000 mm | No | 65 |  | 0
| e) D5 size: 900x3000 mm | No | 72 |  | 0
| f) D6 size: 800x3000 mm | No | 20 |  | 0
| g) D7 size: 700x2500 mm | No | 80 |  | 0
| h) D8 size: 900x2500 mm | No | 20 |  | 0
0
| ALUMINIUM FRAMED CURTAIN WALL |  |  |  | 0
5.04 | Curtain walls shall have strong mullions to withstand wind pressure and shall be anchored to reinforced concrete slab by means of appropriate anchoring devices with contraction allowance slots. Shall have edge covers, skirting and cornice at connection to floor slabs. Top and bottom of curtain walls above the roof shall be covered with aluminum coping and flashing including the concrete parapet. It shall be also Self-cleaning high performance solar control and low-emissivity glass. It should be dual coated glass (thermal insulation) self-cleaning on-line coating with photo-catalytic and hydrophilic properties and superior off-line solar control and low-emissivity coating, with high light transmittance, high light reflectance. Price shall include all accessories. |  |  |  | 0
| Glazing shall be double glass 6mm brown tinted glass for internal and external. Color and pattern will be Approved by the Engineer. |  |  |  | 0
0
| a) CW1 | m2 | 395 |  | 0
| b) CW2 | m2 | 355 |  | 0
| c) CW3 | m2 | 145 |  | 0
| d) CW4 | m2 | 365 |  | 0
0
5.05 | SPECIAL DOORS & PASS BOX |  |  |  | 0
| Supply and fix Superior imported steel paper honeycomb cleanroom doors for pharmaceutical Factories. All doors should have high quality hydraulic dampers and slow closers. - All accessories shall be best quality and fulfill ASTM/EN quality standard requirement and to be approved by Engineer prior to fixing. Biometric Access Control System for laboratory entrance doors is required. - Single or double Cleanroom doors have Thickness of 1.2mm Frame and 1.0mm leaf galvanized sheet filled by flame Retardant paper honeycomb or Aluminum honeycomb door. - The view panel of the door could be double glazing or frosted glass, rounded right angle or corners and white or black border. - Price includes all accessories, locks (304 stainless steel handle lock, elbow pressure ball lock or safety pressure bar lock optional with imported brand locks) that can be equipped with electronic interlock, hinges (304 stainless steel) etc... - Sealing Device: door sealing strip and bottom automatically pressing the sealing strip. - Color to be selected by the Engineer from a full range of manufacturer's catalogue as per the drawings and Engineer's approval. Provide, Fabricate & Fix in position completely sealed element but openable when Sterilization, Bio Chemistry, Parasitology PT Production and related clean rooms needs to be ventilated Aluminum Doors and Windows powder coated average thickness 50mm thick High-Strength standard Aluminium Alloy for frames and leaves. The Aluminum material should be first class (Italian or equivalent). Price shall include 6mm thick Double Glazing, visual control panel including all necessary frames, sub frames and with all unstated works all as per given design and Engineers approval. |  |  |  | 0
| Doors: Lockable and must have a vision panel to from the clean rooms, self-closing, should be appropriately labelled as the international biohazard symbols where biohazardous materials are handled, the contact details of the responsible person for the clean rooms and an indication that access to the area is restricted. |  |  |  | 0
| a) Door Size 1600 x 3000mm | No | 22 |  | 0
| b) PASS BOX -Supply, installation, testing, and commissioning of a high-standard, sensor-operated Laboratory Pass Box, designed for through-wall mounting, with the following specifications, External Dimention 1000 mm (W) x 1000 mm (D) x 1000 mm (H) Internal not Lessthan 600x600,Fully welded Grade SS 316L / SS 304 stainless steel with coved/rounded internal corners for ease of cleaning and to prevent particulate accumulation. Surface finish to be smooth, non-shedding, Doors: Double-walled stainless steel (SS 304/316L) doors with thick, toughened, and transparent viewing windows;Door Interlocking System (Sensor-Based): * Type: Electronic, sensor-activated interlocking mechanism. * Functionality: Ensures that only one door can be opened at any given time, preventing direct airflow and maintaining pressure differentials between the two areas. * Sensors: * Door Position Sensors: Non-contact (e.g., magnetic reed, IR, or proximity) sensors on each door to detect open/closed status for the interlocking system. * Indicators: LED indicator lights (e.g., Green for unlocked/safe to open, Red for locked/other door open) on both sides of the pass box to clearly display door status. * Emergency Release: Concealed emergency override mechanism (if permissible by an application, specify requirements). | No | 6 |  | 0
5.06 | Fire rated Door (Self closing) with 60 minutes integrity prosperity and complete with in tumescent seals Price includes if all the necessary, proved by the engineer |  |  |  | 0
| a) Door Size 1000 x 3000 mm (Fire Rated type) | No | 5 |  | 0
0
5.07 | Supply and fix Superior steel paper honeycomb cleanroom doors for pharmaceutical Factories. All doors should have high quality hydraulic dampers and slow closers. - All accessories shall be best quality and fulfill ASTM/EN quality standard requirement and to be approved by Engineer prior to fixing. Biometric Access Control System for laboratory entrance doors is required. - Single or double Cleanroom doors have Thickness of 1.2mm Frame and 1.0mm leaf galvanized sheet filled by flame Retardant paper honeycomb or Aluminum honeycomb door. - The view panel of the door could be double glazing or frosted glass, rounded right angle or corners and white or black border. - Price includes all accessories, locks (304 stainless steel handle lock, elbow pressure ball lock or safety pressure bar lock optional with imported brand locks) that can be equipped with electronic interlock, hinges (304 stainless steel) etc... - Sealing Device: door sealing strip and bottom automatically pressing the sealing strip. - Color to be selected by the Engineer from a full range of manufacturer's catalogue as per the drawings and Engineer's approval. | m2 | 165 |  | 0
0
5.08 | Stainless Steel Railing (H: 1m): Supply and fix SS Grade 304 railing consisting of 50mm dia top rail (2mm thick) and vertical stands. Includes all welding, base plates, cover flanges, and mechanical anchoring. | m2 | 378 |  | 0
0
5.09 | Wall-Mounted Stainless Steel Handrail: 50mm dia (2mm thick) circular pipe Grade 304. Includes SS wall brackets, wall-return ends, chemical anchoring, and all welding/polishing works. | ml | 154 |  | 0
5.1 | Construction of cubicles for washrooms fabricated from HPL (High Pressure Laminate) or aluminium as per the given detail design. Price shall include all civil or related works. | m2 | 915 |  | 0
0
5.11 | Supply and install a high-performance, insulated polycarbonate skylight system, including all necessary framing, flashing, sealants, and fixings. The system shall be designed to meet the specific requirements of a biobank building, considering factors such as temperature and humidity control, UV filtration, and structural integrity. (Spec. High impact resistance is required, Thickness- 25mm, color- Translucent White (Opal), light transmission -min-60%, U-Value: Target a U-value of less than 1.5 W/(m²K). The framing should be designed to support the polycarbonate panels and withstand wind loads and other structural requirements. Ensure adequate drainage is incorporated into the framing design to prevent water ingress.High-quality, durable, and UV-resistant sealants and gaskets to ensure a watertight and airtight seal.Installation shall be carried out by experienced and certified installers . The material requires prior approval of the Engineer before supplying. Price shall include all the necessary RHS truss,frames & supports all the necessary works that makes the skylight tobe completed N:B The area woluld measure in a horizontal projection. | m2 | 170 |  | 0
5.12 | Supply and install imported or equivalent high-quality tempered & frosted double-glazed semi-structural external horizontally visible 10 mm thick curtain wall including doors and openings with high-quality heat and acoustical proofing effect. Incorporating Aluminium border framing system including glazing withstands loads and thermal and structural movement requirements & shall be anchored to reinforced concert slab/ beam by means of an appropriate anchorage device with expansion and contraction allowance slots. On-site measurements shall be taken before fabrication. All joints shall be firmly secured or connected to prevent infiltration of water into the concert surface. The quality and color shall be as per the client's recommendation and approval. The price shall include a lock, frame, and sticker logo. | m2 | 620 |  | 0
| Total carried to Summary |  |  |  | 0
6. PLASTERING WORK
6.01 | Apply three coats of plastering in cement mortar (1:3). Price shall include pre-cleaning and preparation of the surface.
| a) To all internal wall surface | m2 | 12860 |  | 0
| b) To Exposed Beam and Column | m2 | 3852 |  | 0
0
6.02 | Apply two coats of plastering in cement mortar (1:3). Price shall include pre-cleaning and preparation of the surface. |  |  |  | 0
0
| a) To all internal wall surface | m2 | 18043 |  | 0
| b) Grooved plastering to all external wall surface | m2 | 6105 |  | 0
| c) To exposed beams and columns. | m2 | 4552 |  | 0
| d) To Suspended slab soffits | m2 | 22212.42 |  | 0
| e) To Stair soffits | m2 | 850 |  | 0
| f) To Lift Shaft & Shear walls | m2 | 2121 |  | 0
| g) To Gutter | m2 | 304 |  | 0
0
6.03 | Apply Final coats of gypsum plaster to |  |  |  | 0
| a) To all internal wall surface | m2 | 12860 |  | 0
| b) To exposed beams and columns. | m2 | 4552 |  | 0
| c) To Suspended slab soffits | m2 | 22212.42 |  | 0
| d) To Stair soffits | m2 | 850 |  | 0
| e) To Lift Shaft & Shear walls | m2 | 2121 |  | 0
| f) To Gutter | m2 | 304 |  | 0
0
6.04 | Pointing to brick walls | m2 | 922 |  | 0
0
6.05 | Apply one coats of Special smooth surface plastering in BOND IT GRAY PLAST coving adhesive or eqivalent chemical to all plastered surface. | m2 | 12860 |  | 0
| Total carried to Summary |  |  |  | 0
7. FINISHING WORKS
7.01 | 30mm thick cement sand screed finished flooring in mortar mix (1:3).
0
| a) To receive non slippery ceramic floor tiles. | m2 | 1022 |  | 0
0
7.02 | 48mm thick cement sand screed finished flooring in mortar mix (1:3). |  |  |  | 0
0
| a) To epoxy floor tile. | m2 | 7625 |  | 0
0
| b) To receive PVC tile. | m2 | 1226 |  | 0
0
7.03 | 50mm thick cement sand screed finished flooring in mortar mix (1:3). |  |  |  | 0
0
| a) To receive non slippery porcelain floor tile. | m2 | 22420 |  | 0
0
7.04 | Supply and lay 4mm thick Nitoflor or equivalent Monolithic Epoxy floor finish in accordance with manufacturer's instruction complete application.The work shall be executed on subcontractual bases with material and construction warranty to be given by the supplier.Price shall include preparation of surfaces, application surface leveling and all necessary accessory to finish the work and make ready to use. | m2 | 6400 |  | 0
0
7.05 | Ditto but Labs in 2mm thick | m2 | 1225 |  | 0
7.06 | Supply & fix high quality Non slippery Porcelain floor tile of Size 600 x 600 x10mm thick Italian Made or equivalent specified as per the detail drawing. It has to be resistant to Abrasion, frost, stain, chemical attack & color resistant to light. Color and quality shall be approved by the architect. The price shall include all the necessary civil works to finalize the finish. | m2 | 22420 |  | 0
0
7.07 | 10x100mm high porcelain skirting stuck to wall with approved type of adhesive. | ml | 8408 |  | 0
0
7.08 | Supply and lay 300x300x2mm thick PVC Floor Tile including adhessives. Color, size and pattern of tile shall be approved by the Engineers. Price shall include PVC skirting and all civil works. | m2 | 1226 |  | 0
0
7.09 | Supply & fix high quality RAK or equivalent 300x 300x10 mm non-slippery ceramic floor tile for all toilets. It shall be resistant to Surface abrasion,stain,acid & alkline.The Color & Material quality shall be approved by the architect. The price shall include all the necessary civil works to finalize the finish. | m2 | 1022 |  | 0
0
7.1 | 6mm thick and 100mm high Ceramic skirting stuck to wall with approved type of adhesive. | ml | 935 |  | 0
7.11 | Supply and fix best quality RAK or equivalent 300x200x6mm White glazed Ceramic wall tiles stuck to wall with approved adhesive grout thickness and color as approved by the architect. | m2 | 2053 |  | 0
0
7.12 | Apply patterned Cement troweled finished flooring as as per the Engineers instruction, drawing and approved by the architect. | m2 | 420 |  | 0
0
7.13 | 2cm thick imported Balck galaxy GRANITE floor finished for Lobby and exposed floorings bedded on cement mortar (1:3 ) Price includes cement sand mortar . | m2 | 1045 |  | 0
7.14 | 2cm thick imported Balck galaxy Granite Cladding (Walls/Columns): Supply and installation of 20mm thick polished granite slabs, including galvanized steel sub-frame the price includes SS brackets, anchors, joint fillers, and mitered corners. | m2 | 920 |  | 0
7.15 | Supply and fix 220x20mm Granite door sill. Quality, type color & pattern approved by the engineer. Price includes mortar bed grouting and all other necessary works needed to complete the work. | ml | 1410 |  | 0
0
7.16 | Supply and fix 270x20mm Granite window sill cut to appropriate size and mounted on and including 30mm thick cement mortar (1:3) bedding. Price includes making water drip and edge chamfering as shown on the Architectural detail drawing. | ml | 672 |  | 0
0
7.17 | 30mm thick imported type Granite flooring to stair case bedded on and including cement sand mortar mix 1:3 and joints grouted in appropriate color filler setting coat mortar. Pattern and color of the tile shall be approved by the Architect. |  |  |  | 0
0
| - 20mm thick to landing. | m2 | 359 |  | 0
0
| - Tread size 300x30mm | ml | 1218 |  | 0
0
| - Riser size 150x20mm | ml | 1218 |  | 0
0
| - 20x130mm skirting | ml | 195 |  | 0
0
7.18 | 20x100mm high Granite skirting stuck to wall with approved type of adhesive. | ml | 840 |  | 0
0
7.19 | Supply and fix 30x30x3 mm angle Aluminium corner protection up to a height of 150 cm from floor finish level, flushed to column and walls. | No | 1996 |  | 0
0
7.2 | 20mm thick Marbel threshold bedded on & including 30mm thick cement mortar. |  |  |  | 0
0
| a) Width 250mm | ml | 740 |  | 0
0
7.21 | Diameter 40cm open half ditch laid on compacted selected fill connected with cement sand mortar. | ml | 330 |  | 0
0
7.22 | Supply and fix Coved Indoor Wall Panel for wall protection fixed to walls at height of 150cm that is fabricated from Solid Phenolic or equivalent flexible PVC material with minimum Size: 125*20mm | ml | 1692 |  | 0
0
7.23 | Supply & Lay 3mm thick Vinyl or linoleum flooring at microbiology and clean rooms as per manufacturer standards and Engineers approval. The work is to be carried out by specialized sub-contractors. Price Shall include Covings between floor and wall. A minimum of 10 years guarantee is required. | m2 | 1235 |  | 0
0
7.24 | Construction of Coving (Quarter Circle) by plastic or rubber or appropriate material as per Engineers approval at every corner of clean rooms to avoid bacterial or contaminant accumulation and maximizing the capacity of regular cleaning to make curved edges. Note: There is no sharp corner or 90o between wall to wall, wall to column and wall to ceiling. | m2 | 388 |  | 0
0
7.25 | Supply and fix custom-sized, thick for outside & thin transparent inside double and luxurious drapery or curtain for office windows as per Engineers approval. Price shall include all necessary accessories such as rods, tiebacks, holdbacks, rings, clips, finials and all unstated accessories related to curtain works. Color shall be approved by client. | m2 | 1300 |  | 0
7.26 | Construct C-25 reinforced concrete 100mm thick broom finished concrete pedestrian (light duty) walkway around the buildings with single mesh of diameter 8mm spacing 200x200 mm casted on top of 150mm quarry waste + 250mm sub-base layers. with C-25 100 x 200mm lateral precasted concrete curbstone of straight and smootly finished. | m2 | 5400 |  | 0
7.27 | Supply and installation of high-performance acoustic roof /wall insulation system designed to reduce airborne noise and flanking transmission,Semi-rigid high-density Rockwool or Mineral Wool batts (minimum density 80kg/m3 ) | m2 | 2300 |  | 0
| Total Carried to Summary …………… |  |  |  | 0
8. PAINTING WORK
Painting work shall includes all surface pre-cleaning by chiseling the wall , preparation of finish, polishing, safe scafolding and cleaning at the end of finishing work; Nominal thickness of 100mm (or as specified), fitted tightly between rafters/purlins.
8.01 | Apply three coats plastic emulsion paint to internal plastered wall surface equivalent to JOTUN paint |  |  |  | 0
| a) To all internal wall surface | m2 | 18043 |  | 0
| b) To exposed beams and columns. | m2 | 3852 |  | 0
| c) To Suspended slab soffits | m2 | 22212.42 |  | 0
| d) To Stair soffits | m2 | 850 |  | 0
| e) To Lift Shaft & Shear walls | m2 | 2121 |  | 0
8.02 | Apply three coats oil(synthetic) paint to internal plastered wall surface. |  |  |  | 0
| a) To all internal wall surface | m2 | 12860 |  | 0
| b) To exposed beams and columns. | m2 | 2960 |  | 0
8.03 | Contextera paint to external walls, beams and columns the price shall include all the layers of the manifacturer instruction & it reqires prior approval of the Engineer |  |  |  | 0
0
| a) To all external wall surface | m2 | 6105 |  | 0
0
| Total Carried to Summary |  |  |  | 0
9 | SANITARY INSTALLATION
9.1 | SANITARY FIXTURES
All fixtures and pipes which are specified below shall subject to the Consultants or Owner's approval based on samples, brochures and catalogues presented by the contractor. Unit Price shall include all the necessary fixing brackets or hooks and all assistnace civil works such as chiselling of walls, floors, beams etc…
9.1.1 | VANITY TOPS HAND WASH BASINS
| 25mm thick granite top in polished granite with post formed edges for vanity tops (bull nosed for visible edges) including forming approximately 500 mm diameter openning for sink bowl. Price includes all steel framing on cabinets for fixing of unit, cabinets, vanity, oval hand wash basin bowl made of vitreous china with concealed front overflow, mounting hardware, template & sealing compound,. It shall consist plug, P-smell trap with connection pipe and all other necessary accessories. |  |  |  | 0
| Double bowl size (1475 X 600 ) | No. | 28 |  | 0
9.1.2 | HAND WASH BASINS |  |  |  | 0
| Supply and fix Hand Wash Basin made of white vitreous China ceramics with milano or equivalent chrome plated cold & hot water wrist action handle mixing tap & pedestal. The fixture shall conform to BS5506-3 or equivalent institution. The taps, chrome plated brass p-trap, waste fittings, connecting pieces, fixing & supporting elements and other accessories which complete the set shall comply with the relevant clauses of BS standard or equivalent institution. |  |  |  | 0
| a) 550 x 450mm normal | No | 1 |  | 0
9.1.3 | HAND WASH BASINS FOR DISABLES |  |  |  | 0
| Ditto as item no. 9.1.2 but for disabled (assisted ) hand wash basin with manufactured grab rails and all other accessories as per BS or ISO standards. | No | 14 |  | 0
9.1.4 | WATER CLOSETS |  |  |  | 0
| Supply and fix Water Closet (WC) of wash down action,floor mounted (S-Trap), close coupled, made of white vitreous China ceramics. The fixture shall conform to BS5503-2 or equivalent institution. The plastic seat cover, low flush cistern, waste fittings, connecting pieces, fixing & supporting element and other accessories which complete the set shall comply with the relevant clauses of BS standard or equivalent institution. Price shall also include hand held bidet spray (Shut up hose) of approved quality complete with head, flexible hose and all other necessary accessories |  |  |  | 0
| a) Size 680 x 365mm | No | 57 |  | 0
9.1.5 | TURKISH WATER CLOSET |  |  |  | 0
| Dismantle the exiting damaged turkish type water closet and replace with new Turkish type high level wash down water closets made of white vitreous china with flushing cistern including all necessaryaccessories (Price shall include all the necessary assistnaces, works such as chiseling of walls, floors, beams and unscrew fitttings and transporting the old fixtures and hand over to the client etc) Sample approavl is mandatary. | No | 52 |  | 0
9.1.6 | WATER CLOSETS FOR DISABLES |  |  |  | 0
| Supply and fix approved quality, assisted (Disabled ) water closet as per specifciation with grab rails. Price shall include wash down action,floor mounted (S-Trap), close coupled, made of white vitreous China . The grab rails, supports, plastic seat cover, low flush cistern, waste fittings, connecting pieces, fixing & supporting element and other accessories which complete the set shall comply with the relevant clauses of BS standard or equivalent institution. Price shall also include hand held spray (shut up) flexible hose of approved quality complete with head, flexible hose and all other necessary accessories | No | 14 |  | 0
9.1.7 | TOILET PAPER HOLDER |  |  |  | 0
| Supply and fix Toilet Paper Holder made of white vitrous china (BS3402), of approved quality complete with all the necessary fixing accessories. |  |  |  | 0
| a)Size 185 x 115mm | No | 123 |  | 0
9.1.8 | TOWEL HANGER |  |  |  | 0
| Supply and fix approved quality Towel Hanger made of chrome plated copper alloys, single tubular, surface mounted,bar length of 600mm with 3mm minimum thickness near shower and assisted baths complete with fastening screws white vitreous china ceramic support and other accessories. | No | 5 |  | 0
9.1.9 | SOAP HOLDER |  |  |  | 0
| Supply and fix RAK or equivalent Soap Holder , approved quality made of white vitrous china ceramics (BS3402), for shower units complete with all the necessary accessories. |  |  |  | 0
| Size 225 x 110mm | No | 5 |  | 0
9.1.10 | Hand Held Bidet Sprayer (Shattaf)
| Supply and fix 150cm long polished chrome hand held bidet spray of approved quality of adjustable switch with brass valve‎(main body is brass), brass nozzles complete with head, flexible stainless steel hose and all other necessary accessories. | No | 123 |  | 0
9.1.11 | SOAP DISPENSER |  |  |  | 0
| Supply and fix ASD/ASDR or its equivalent press type soap dispenser of the following characters at each toilet room and hand washing facilities. - splash proof - double insulated - installation fixings supplied - tray supplied - vandal resistant | No | 71 |  | 0
9.1.12 | CRYSTAL GLASS MIRROR |  |  |  | 0
| Supply and fix stylish framed crystal glass mirror for hand wash basins with copper back protection, including chrome plated brass mirror clips with chrome plated screws & etc. |  |  |  | 0
| a) 500 x 400mm | No | 15 |  | 0
| b) 1475 X 600mm | No | 28 |  | 0
9.1.13 | SHOWER TRAY |  |  |  | 0
| Supply and fix shower units made of enamelled heavy duty cast iron shower tray, complete with approved quality level controlled mixing valve, fixed & flexible shower head, P-smell trap and with all other necessary accessories. |  |  |  | 0
| a) 700 x 700mm | No | 5 |  | 0
9.1.14 | EMERGENCY SHOWER & EYE WASH |  |  |  | 0
| Supply and install approved quallity floor mounted emergency shower and eye wash with stainless steel drench rose fed by a full bore stay open valve operated by a rigid pull handle with a combination of face/eye wash fountain with stainless steel bowls. The shower tubulars ,valves ,fitting and linkages shall be stainless steel.Complete with all the necessary accessories. | No | 3 |  | 0
9.1.15 | MOP SINK (Janitor Sink) |  |  |  | 0
| Supply and fix 635x546x600mm Eagle floor mounted mop sink model # F1916 or equivalent constructed of type 304 stinless steel with drain and flat strainer plate. Comprising: 4 pole mop holder, 610x102mm 25mm projection, model# 321561, Hose and Bracket length = 762mm model# 312689, Service Faucet with vacuum breaker model# 312690 | No | 10 |  | 0
9.1.16 | KITCHEN SINK |  |  |  | 0
| Supply and fix aqua or equivalent stainless Steel Kitchen Sink with double bowl as where shown on the drawing. Complete with milano or equivalent cold and hot water mixing tap, chrome plated chain, flex-italy or equivalent flexible hoses, plug, P-smell trap, 60cm long flex-italy or equivalent flexible hoses and with all other accessories. | No | 2 |  | 0
9.1.17 | URINALS |  |  |  | 0
| Supply ,fix,test & commission low consumption,wall mount Urinals made of white vitreous china. The fixture shall consist waste fittings, connecting pieces, fixing & supporting elements, automatic battry operated flushing tap & all other necessary accessories which complete the set. Price shall include aluminium or fiberglass urinal particion of size 360mm at top, 185mm at bottom and 700mm length etc, Colour: white | No | 28 |  | 0
9.1.18 | WATER HEATER |  |  |  | 0
| Supply and fix Ariston or equivalent Electric Water Heater with a capacity given below.Complete with all water proofing, mounting and fastening material, safety, one-way valve, approved quality coil and gate valve and with all the accessories.Heat preservation hot water tank in gallbladder,thickness 1.0mm, outer covering thickness 0.6mm,foam polyurethane 50mm thick, outside protective layer: stainless steel. Price shall also include 60cm long flex-italy or equivalent flexible hoses. |  |  |  | 0
| a) Capacity 50 Liter | No | 3 |  | 0
| b) Capacity 80 Liter | No | 4 |  | 0
9.2 | WATER SUPPLY PIPES AND VALVES |  |  |  | 0
9.2.1 | Supply, lay install and commission approved quality PPR pressure pipes (PN20),for hot & cold water distribution system to sanitary fixtures. The pipes shall be complete with all the necessary connecting pieces such as bends,Ys, Ts, reducers, nipples, unions, hangers & supported with compatible clips all as per manufacturer's recommendation to the walls, floors, slabs,beams, ceilings, etc…Unit price shall include, disinfection of the pipes with Chlorine and all the necessary assistance to the installation works. The installation shall be tested at a pressure of 20kg/cm2 at the expense of the contractor. The pipes and fittings shall conform to BS3505/DIN8062 or equivalent institution.The PPR pipe shall be UV resistant at the exposed areas. Pipe sizes are external. |  |  |  | 0
| Dia 20 mm | ml | 622 |  | 0
| " 25 " | ml | 449 |  | 0
| " 32 " | ml | 253 |  | 0
| " 40 " | ml | 79 |  | 0
| " 50 " | ml | 101 |  | 0
| " 63 " | ml | 33 |  | 0
| " 75 " | ml | 35 |  | 0
9.2.2 | Supply and fix chrome gate Valves of approved standard, on water supply distribution lines where shown on the drawing The valves shall be compatable with PPR pipes and complete with adaptors,unions, elastic water proofing , hand wheels of normal quality and all other necessary accessories. |  |  |  | 0
| Diameter 20mm | No | 5 |  | 0
| Diameter 25mm | No | 17 |  | 0
| Diameter 32mm | No | 14 |  | 0
| Diameter 40mm | No | 4 |  | 0
| Diameter 50mm | No | 3 |  | 0
9.2.3 | Supply, fix, test and commission Bronze Gate valves, PN 16, of approved Standards & quality, and the same brand of the pipe, on the water supply Riser Branch lines to rooms with sanitary provissions, as where shown on the drawings. Complete with all required fittings and accesseries there to. |  |  |  | 0
| Diameter 32mm | No | 5 |  | 0
| Diameter 40mm | No | 5 |  | 0
| Diameter 50mm | No | 4 |  | 0
| Diameter 63mm | No | 3 |  | 0
| Diameter 75mm | No | 4 |  | 0
9.2.4 | Supply and fix chrome plated Service (Angle) Valves (PN16) of approved standard before hand wash basin, water closets and sinks, which must be compatable with PPR pipes. The valves shall be complete with adaptors, unions, elastic water proofing, hand wheels of approved quality and all other necessary accessories. | No | 285 |  | 0
9.2.5 | Supply and fix AIR RELEASE VALVE , complete with bronze gate valve before & all required fittings on top of water risers as shown on the riser diagram. |  |  |  | 0
| Diameter 25mm | No | 3 |  | 0
9.2.6 | PRESSURE REDUCING VALAVE |  |  |  | 0
| Supply ,fix ,test , and commission approved quality pressure reducers on water supply pipes, including accessories as where shown on the drawings. The work shall be carried out in accordance with the technical specification and manufacturers instruction .unit Price shall also include bronze gate valves after and before reducers and pressure gauges before & after pressure reducers. Max. pressure range : From 10 bar to 15 bar |  |  |  | 0
| Sizes : a) 32 mm | No | 4 |  | 0
| b) 40 mm | No | 2 |  | 0
| c) 50 mm | No | 2 |  | 0
9.3 | FIRE FIGHTING SYSTEM |  |  |  | 0
9.3.1 | 48m3 GRP WATER TANKS FOR FIRE WATER |  |  |  | 0
| Supply,mount,test & commission Hot Press Molded sectional GRP(Glass reinforced plastic) externally braced water. Tanks for water storage tanks.Complete with: |  |  |  | 0
| - Panel size (Insulated)…1.15m x 1.15m, thckness 4.5mm |  |  |  | 0
| - All connecting pieces & flanges (On drain, over flow, suction pipes) |  |  |  | 0
| - 800x800mm properly hinged access door with insect proof air vent, lockable. |  |  |  | 0
| - GRP internal ladder & Aluminum external access ladder. |  |  |  | 0
| - Appropriate water level indicator (Cat and Mouse indicator) |  |  |  | 0
| Type : AQUASTOW--- A.C. Plastic Industries Lim or equivalent. |  |  |  | 0
| -Price shall inclde all is acessories of vent pipe, inlet, outet, drain, overflow pipe, float valve, level control swich and all other accessories as per the drawing. |  |  |  | 0
| a) Size: 6.15 x 4.15 x 2.0 meters (Total volume = 48m3 ) | No | 1 |  | 0
9.3.2 | Supply,install,test & commission factory assembled fire protection pump set as per NFPA-20 requirments & specification given below. Pump shall be factory tested & performance data to be recorded & submitted to demonstrate its compliance with the pump specification. |  |  |  | 0
| The operation of the electric pump shall be arranged to be based on pressure demand . In addition there shall be one jockey pump to compensate minor leaks which shall be operational by its own pressure switch. Pumps shall be mounted on anti vibration rubber or spring mountings on a common frame to avoid vibration transmission to the building structure. There shall also be a diesel driven fire pump complete with its controller to be arranged inline with the electric pumps/start operating automatically when the electric pump stops/ and to be installed on a common frame with the electric pump sets which shall be operational during mains power failure. The diesel engine shall have proper cooling mechanism, exhaust manifold to out side the pump house, day tank at least required for one hours operation, and shall have its own DC battery. Three sets of Full catalogue dealing with operation maintenance and installation details including the proper wiring diagram shall be included with in the supply. |  |  |  | 0
| Detail requirement |  |  |  | 0
| Electric fire pump sets |  |  |  | 0
| a)Electric fire pumps |  |  |  | 0
| i- Material : |  |  |  | 0
| - Housing … Cast iron |  |  |  | 0
| - Impeller …. Cast iron |  |  |  | 0
| - Shaft …… Stainless steel |  |  |  | 0
| - Seal …….. Mechanical seal |  |  |  | 0
| - Motor …….. Three phase self ventilated |  |  |  | 0
| b -Electric pump controller |  |  |  | 0
| Shall incorporate the following |  |  |  | 0
| - Isolation switch, power available indicator, alarm and signal device, |  |  |  | 0
| water pressure sensor connection for each pump,and with all |  |  |  | 0
| necessary system protection devices. |  |  |  | 0
| The sequential timing device shall prevent any one motor from |  |  |  | 0
| the controller shall start the pumps at a minimum interval of 3 to 5sec. |  |  |  | 0
| Diesel pump sets and controller |  |  |  | 0
| The Fire pump that shall be driven by the diesel engine shall have similar feature with the electric fire pump sets. |  |  |  | 0
| The controller shall have the facility to start the engine automatically in case of main power failure and system pressure drop and stop the engine after a preset time lag when mains power resumes. |  |  |  | 0
| The Engine battery shall have automatic battery charging facility from the AC line with an audible alarm in case of power failure. |  |  |  | 0
| Pumps performance requirement |  |  |  | 0
| The required duty point of the pumps set shall be as follows. |  |  |  | 0
| a- One electric pump with their controller |  |  |  | 0
| Capacity : Flow rate (Q) =8 liter/second |  |  |  | 0
| Head ( H ) = 70 meters each |  |  |  | 0
| b - Electric Jockey pump |  |  |  | 0
| Capacity : Flow rate (Q ) = 1.5 liter/ sec. |  |  |  | 0
| Head ( H) = 75 meters |  |  |  | 0
| c - Diesel pump with the diesel engine and controller |  |  |  | 0
| Capacity : Flow rate (Q ) = 8 liter/sec. |  |  |  | 0
| Head ( H ) = 70 meters |  |  |  | 0
| d - Operation voltage shall be 380/50/ 3phase, and site altitude is 2750 meters | Set | 1 |  | 0
8.3.3 | Supply, install, test and commissioning fire water supply of schedule 40 galvanized steel piping including pipe fittings, supports anchors, and necessary accessories, all as per the technical specifications 3964 & NFPA requirements. The installation shall be tested at a pressure of two times the highest working pressure of firefighting pumps for a period of at least 2hrs with no leakages of water. The GS pipes, accessories, fittings &method of connection of up to Dia.50mm shall be screw connection and above grooved shall comply with the requirement BS 4991& BS6920 part 2 &3 or equivalent specification. |  |  |  | 0
| Diameter 25 mm | ml | 740 |  | 0
| " 32 " | ml | 430 |  | 0
| " 40 " | ml | 220 |  | 0
| " 50 " | ml | 145 |  | 0
| " 63 " | ml | 48 |  | 0
| " 75 " | ml | 30 |  | 0
| " 90 " | ml | 135 |  | 0
9.3.4 | Supply, install, test & commision spray type Sprinkler Head with 1/2 nominal discharge orifice. Ordinary temperature rating shall be 160ºF - 175ºF throughout except where special conditions exist. The material and installation shall comply with the requirements of NFPA 13 &/or equivalent institution |  |  |  | 0
9.3.4.1 | Pendant sprinkler nozzels |  |  |  | 0
| Nominal orfice Size 1/2'' |  |  |  | 0
| K (factor) =80 |  |  |  | 0
| Temperature rating =68°C @STD. Response |  |  |  | 0
| Pressure rating =0.5BAR | No | 299 |  | 0
9.3.4.2 | Pendant sprinkler nozzels(Kitchen) |  |  |  | 0
| Nominal orfice Size 1/2'' |  |  |  | 0
| K (factor) =80 |  |  |  | 0
| Temperature rating =93°C @QR. Response |  |  |  | 0
| Pressure rating =0.5BAR | No | 25 |  | 0
9.3.5 | Drain & test valves for all control valves , including all connecting pieces. |  |  |  | 0
| a) Dia. 50 mm | No | 7 |  | 0
0
9.3.6 | Air release valves , including service valve & all connection pieces. |  |  |  | 0
| Diameter 40 mm | No | 3 |  | 0
9.3.7 | Supply and mount 5kg Fire Extinguishers of carbon dioxide type inside kitchen, lab, corridor and fire hazard potential rooms complete with brackets and all approved standards (exceptionally effective on class B, C & E fire). Unit price shall include all the necessary assistance work. | No | 48 |  | 0
9.3.8 | Supply and fix recessed wall mounted Fire Hydrant Hose reels as per BS EN671-1. Complete with dia. 40 mm and 32 meters long canvas hose, spray jet nozzle, bronze gate valve, swinging guide arm, and with all other necessary accessories.Cabinet shall be factory made 1.2mm thick pretreated electro galvanized steel sheet, painted with electrostatic powder coating and oven backed at min.180 degree cent with easily openable glass door of size shall be about 900 x 600 x 250mm /approximate.size/. Price shall include angle valve,pressure reducer & fire extinguisher 5kg weight ABC Chemical powder in side cabinet. | No | 12 |  | 0
9.3.9 | Testing & commissioning |  |  |  | 0
| Testing & commissioning of all the above fire protection system,including fire suppressions & site fire water distribution system shall be done according to the technical specification & NFPA requirments & shall be done by certified personnels . Supplying of required testing instruments ,labourers,etc shall be the responsibility of the specialised sub contractor. | Ls | 1 |  | 0
9.4 | WASTEWATER PIPES AND ITS ACCESSORIES |  |  |  | 0
| All domestic waste, vent and storm water pipe lines shall be uPVC pipes and shall be provided with a minimum slope as indicated on the drawing towards the outlet unless specified. All uPVC pipes and necessary fittings shall be standard quality and be free from damage during storage, transportation, construction etc. Unit price shall include all the necessary assistance civil works, such as excavation cartaway, fixing or hanging to walls, beams or slabs. etc., necessary fittings such as bends, Y, T, etc. Storm water PVC pipes shall resist the external temperature and the quality shall meet the purpose. |  |  |  | 0
9.4.1 | Providing, laying and jointing of internal uPVC PN-6 waste pipes with all uPVC pipe fittings including jointing with solvent cement joints and testing of joints etc. according to where shown on the drawings. Complete with all the necessary fittings. Provide cleaning detail for all waste water riser pipes as per the detail drawing. |  |  |  | 0
| a) Diameter 50 mm | ml | 689 |  | 0
| b) Diameter 75 mm | ml | 384 |  | 0
| c) Diameter 110 mm | ml | 463 |  | 0
| d) Diameter 160 mm | ml | 75 |  | 0
9.4.2 | Ditto as Item No 9.4.1 but Vulcathene Pipes for the chemical wastes from the lab. sinks and bed pan washing sinks of the following pipe sizes. |  |  |  | 0
| a) Diameter 50 mm | ml | 117 |  | 0
| b) Diameter 75 mm | ml | 108 |  | 0
| c) Diameter 110 mm | ml | 23 |  | 0
9.4.3 | BRASS FLOOR DRAIN |  |  |  | 0
| Removing existing floor drains and replacing them by new Anti-clogging, Anti-Odor, Mothproof, Rust-proof, Drainage, Filte brass electroplated box of approved quality, complete with P-smell trap with 6cm water seal, treaded drain/clean bottom outlet, and all other necessary fittings, accessories, works and materials. |  |  |  | 0
| Size:- Dia. 100 x 100 x 75mm | No | 68 |  | 0
9.4.4 | Supply and fix vent caps made of rigid uPVC to be connected to the roof terminal of vent pipe. Unit price shall include flushing works to prevent roof leakage: - |  |  |  | 0
| a) Size: - Dia.50mm | No | 3 |  | 0
| b) Size: - Dia.110mm | No | 4 |  | 0
9.4.5 | Supply & fix clean outs made of rigid plastic PVC cap where shown in the drawing. |  |  |  | 0
| Diameter 75 mm | No. | 38 |  | 0
9.5 | ROOF RUNOFF DRAINAGE SYSTEM |  |  |  | 0
9.5.1 | Supply and fix uPVC Downpipes min. wall thickness 3.2mm,with mass concrete support at ground level and complete with basket strainer at inlet, galvanized clips at every elbows,joints and at every 1.5m interval complete with all accessories.The pipes, accessories, fittings & method of welding shall comply with the requirement of BS 4514or equivalent Institution. Unit price shall include all the necessary assistances to the installation works. |  |  |  | 0
| a) Size: - Dia.75 mm | ml | 36 |  | 0
| b) Size: - Dia.110 mm | ml | 1052 |  | 0
9.6 | WATER PROOFING FOR WET ROOMS & OTHERS |  |  |  | 0
9.6.1 | Apply Xypex or equivalent cementious water proofing material for toilet room floors & to a height of 300mm on walls and columns as per the manufacturer's instruction. The cost shall include cleaning of all dirts, trace of grease, oil and loose particles. The work shall be done on subcontractual bases with the supplier of the material which will give material & construction gurantee to the client. | m2 | 780 |  | 0
9.6.2 | Apply APP modified & thickness not less than 4mm slated finish Water Proofing Membrane or compatible equivalent material for R.C retaining wall in basement and semi-basement floors as per the manufacturer's instructions and recommendations as shown on the drawing. The cost shall include cleaning of all dirts and dust materials and all incidental works and details of manufacturer. The work shall be done on subcontractual base with the supplier of the material which will give material and construction guarantee to the client . | m2 | 430 |  | 0
9.7 | SUB SURFACE DRAINAGE SYSTEM |  |  |  | 0
9.7.1 | Supply and lay purpose madedia. 160 uPVC , PN-6 Factory made perforated pipe to BS 1194:1969 for subsoil drainage system around the building according to where shown on the basement floor plan and detail drawing . |  |  |  | 0
| Unit price shall include: |  |  |  | 0
| - filling and spreading of coarse gravel, fine gravel, sand and selected backfill to an average depth of 5.0meters and average width of 1.2 meteras per the detail drawing. |  |  |  | 0
0
| - 4mm thick Watergum or equivalent 4mm thick water proofing membrane coating forall the buried the shear wall of first and second basement arround all its perimeters in accordance with the drawing. |  |  |  | 0
| - Bitu board or equivalent covering material to cover the water proofing; or single layer Brick wall in accordance with the drawing. |  |  |  | 0
| - 60cm well compacted clay soil on the top |  |  |  | 0
| - All other necessary connecting pieces and civil work assistances. | ml | 244 |  | 0
9.7.2 | Providing, laying and jointing of internal uPVC PN-6 waste pipes with all uPVC pipe fittings including jointing with solvent cement joints and testing of joints etc. according to where shown on the drawings. Complete with all the necessary fittings for connecting each floor gulleys to pump sum as per the basement sanitary drawing provided. Price shall include four bronze double BACK FLOW PREVENTER VALVE complete with bronze gate valve before it and as instructed on site. |  |  |  | 0
| Diameter 110 mm | ml | 51 |  | 0
9.7.3 | Supply and install factory made stainless steel flloor gully, of bar grating with deep Seal Floor Gully type or equivalent, comprising component deep seal floor gulley with channel for basement floor drainage system complete with all necessary accessories. size 300x300mm | No | 12 |  | 0
9.7.4 | Supply and coat Watergum or equivalent standard type 4mm thick non slated bituminous water proffing as per manufacturers instruction under basement floor slab btween 75mm thick C-10 screed. Price shall include two layers C-10 concrete screed. | m2 | 2764 |  | 0
9.7.5 | Pump sump |  |  |  | 0
| Construct pump sump out of reinforced conceret as per the sanitary detail drawing and structural drawing to be given on site. Price shall incude form work,excavation ,heavy duty cast iron manhole cover and frame to BS27899 (non ventilated) and all civil assistance works. The contractor shall be fully responsible to coordinate the pump sump sanitary & structural details & location before casting any concrete structure in the basement. Price shall include xypex or equivalent internal water proofing work as per the detail drawing provided. |  |  |  | 0
| Size (average) --- 1.8 x 1.8 meter and 2m depth | No | 2 |  | 0
9.7.6 | Submersible Pump |  |  |  | 0
| Supply,fix,test and commission europe manufactured submersible (dewatering) pump as where shown on the drawing, manufacturer's instruction and detail drawing given. |  |  |  | 0
| Price shall include float swicth (level swicth to start and stop the pump on the predetmed water level), valves(one-way and stop valves) , dia.50mm HDPE PN-16 pressure discharge pipe up to the nearest storm water drainage point as shown on the drawing and all other necessary accessories required for the proper functioning of the system |  |  |  | 0
| Q = 5 l/sec. |  |  |  | 0
| H = 40 meters | No | 4 |  | 0
9.7.7 | Supply & lay cleaning eye on each corner of the sub |  |  |  | 0
| soil drainage system as where shown on the drawings. |  |  |  | 0
| Provide plug or screw tube plastic cap on top to external |  |  |  | 0
| ground level. Price shall include fittings and every necessary items that complete the work. |  |  |  | 0
| Diameter 110mm | ml | 16 |  | 0
9.8 | SITE WATER SUPPLY SYSTEM |  |  |  | 0
9.8.1 | Pipe Work |  |  |  | 0
| Supply ,lay ,test ,disinfect and commission HDPE PN 16 Water distribution pipe; including necessary fitting, excavation to an average depth of 800mm & a width of 600mm & 100mm thick sand bedding all around the pipe, backfilling etc.and all as per the detail drawings and technical specification. All HDPE domestic water pipe. Pricce shall include connection adaptor with the GS pie. sizes given below are external diameter |  |  |  | 0
| With compression connection outer diameter |  |  |  | 0
| Dia 75mm (from Municipal water main to GRP tanks). | ml | 80 |  | 0
9.8.2 | Valves |  |  |  | 0
| Supply, install, test, and commission European standard (Manufactured) Bronze Gate Valve on the water supply pipe as where required and shown on the drawings. |  |  |  | 0
| Dia. 75 mm | No | 3 |  | 0
9.8.3 | Valve box |  |  |  | 0
| Construct single brick masonry valve box bedded in cement sand mortar with proportion of 1:3 including R-C-base slab & R-C cover.Price shall also include excavation of pit , cartaway and backfilling. |  |  |  | 0
| Size = 0.6 x 0.6 x 1.0m | No | 3 |  | 0
9.8.4 | Construction of thrust blocks (C-20 Mass concrete) just at every horizontal bend, vertical bend, Tee connection, Elbows and as per the detail drawing or by direction of the Engineer. Location of thrust blocks shall be determined on site. | m3 | 0.5 |  | 0
9.8.5 | 70m3 GRP WATER TANKS FOR FIRE WATER |  |  |  | 0
| Supply,mount,test & commission Hot Press Molded sectional GRP(Glass reinforced plastic) externally braced water. Tanks for water storage tanks.Complete with: |  |  |  | 0
| - Panel size (Insulated)…1.15m x 1.15m, thckness 4.5mm |  |  |  | 0
| - All connecting pieces & flanges (On drain, over flow, suction pipes) |  |  |  | 0
| - 800x800mm properly hinged access door with insect proof air vent, lockable. |  |  |  | 0
| - GRP internal ladder & Aluminum external access ladder. |  |  |  | 0
| - Appropriate water level indicator (Cat and Mouse indicator) |  |  |  | 0
| Type : AQUASTOW--- A.C. Plastic Industries Lim or equivalent. |  |  |  | 0
| -Price shall inclde all is acessories of vent pipe, inlet, outet, drain, overflow pipe, float valve, level control swich and all other accessories as per the drawing. |  |  |  | 0
| a) Size: 9.15 x 4.15 x 2.0 meters (Total volume = 70m3 ) | No | 1 |  | 0
9.8.6 | DOMESTIC WATER PUMP |  |  |  | 0
| Variable Frequency Drive ( VFD ) Pumps |  |  |  | 0
| Supply, fix, test and commission approved quality surface centrifugal pumps fitted with variable speed control motors which enable the system to provide constant output pressure whatever the demand.All set should be complete and ready for installation including a tripple of pumps of the capacity as stated below that incorporate an integral frequency converter and can easily be mounted in the basement with valves, pressure sensors, control panel & cabinet, and all other necessary accessories. |  |  |  | 0
0
| The variable speed for the drive motor shall be achieved by a variable frequency controller and shall be designed and installed to work as complete operational package with the pressure sensors. |  |  |  | 0
0
| To satisfy the peak demand, the pressure sensor should enable the standby pump to work in parallel and to turn off these pump during low demand. |  |  |  | 0
0
| When the pump is started the VFD drive shall check and ensure that the motor is at rest, before accelerating the motor in the correct direction. |  |  |  | 0
| To prevent damage to the VFD electronic over current protection shall be incorporated to protect against over current due to output short circuits. The electrical feeder to the VFD shall incorporate a bypass circuit, so that the VFD can be bypassed. In addition minimum switch off level should be set to protect the pump from dry running. |  |  |  | 0
| a- Suction & delivery manifolds made from stainless steel. |  |  |  | 0
| b- An isolating and non-return valves which shall be fitted |  |  |  | 0
| between the discharge manifold and individual pumps. |  |  |  | 0
| c- Control cabinet/automatic cascade control/ with all the |  |  |  | 0
| necessary components and integrated frequency converter |  |  |  | 0
| mounted on the same frame as the pumps. |  |  |  | 0
| d- The system shall maintain a constant pressure though |  |  |  | 0
| continuously variable adjustment of the speed of the pumps |  |  |  | 0
| connected. |  |  |  | 0
| e- The pump changeover shall be automatic and depending on the load, operating hours, fault, etc. |  |  |  | 0
| f- Dry running protection either with level switch or similar |  |  |  | 0
| protection system. |  |  |  | 0
| g- Factory made expansion joints on suction & delivery pipes to isolate structure borne noise in pipe works , absorption of |  |  |  | 0
| thermal expansion and contraction, etc. |  |  |  | 0
| h- Diaphragm (pressure vessel) tank ,10 bar , 100 liter capacity |  |  |  | 0
| i- Two pumps operate in a cascade manner & the third one |  |  |  | 0
| shall be stand by pump. |  |  |  | 0
| k - All necessary accessories for the proper operation of the |  |  |  | 0
| boosting system, including pressure gauges, safety valves, |  |  |  | 0
| operating light for each pump, valves manifolds, etc |  |  |  | 0
| The work shall be carried out in accordance with the |  |  |  | 0
| manufacturer's instruction, technical specification and |  |  |  | 0
| manufacturer's instruction and drawings. |  |  |  | 0
| The pumps should have the following capacities. Discharge, Q = 4 l/s Head, H = 60 m (One set contains three pumps plus one pressure vessel) | Set | 1 |  | 0
9.8.7 | SEWER PIPE |  |  |  | 0
| Supply,lay,test & commission uPVC,PN-6 waste drainage pipes to an average depth of 800mm according to the drawing shown with a minimum slope of 1% or as inicated on the sanitary site work on a firm bed granular material of 100mm below and 200mm above the crown of pipe as shown on the detail drawing.The joints shall be made tight and installation shall make the best condition for cleaning and maintenance.For pipe laying follow manufacturer's instruction & technical specification. |  |  |  | 0
| a) Dia.110 mm | ml | 57 |  | 0
| b) Dia.160 mm | ml | 345 |  | 0
9.8.8 | ACID RESISTANT SEWER PIPE |  |  |  | 0
| Ditto as Item No 9.8.7 but Vulcathene site Pipes for the chemical wastes from the lab. sinks and bed pan washing sinks of the following pipe sizes. |  |  |  | 0
| a) Dia.110 mm | ml | 145 |  | 0
9.8.9 | CONSTRUCTION OF INSPECTION MANHOLES |  |  |  | 0
| Construct rectangular manhole out of 250mm thick double brick walls, internal dimension 600mm x 600mm x 800mm (average depth), internally plastered with cement / sand mix ratio of 1:3 mortar on a base of C - 25 R.C slab size,100 x 100x 10cm, including benching and bottom channeling with C-15 mass concrete. Slab shall be reinforced with diameter of 10mm reinforcement bar c/c 200mm both ways. Provide 150mm thick granular materials beneath the slab and properly compact to the satisfaction of the Engineer. Manhole shall have C - 25 pre-cast R.C cover slab size, 2 x (1/2 x Ø) 60cm x 8cm, reinforced with a diameter of 8mm reinforcement bar c/c130mm in both ways, including a diameter of 14mm solid steel bar ring for handle with a diameter of 16mm supporter bar, all in accordance with the given detail drawings. Manhole construction shall be according to the detail drawings |  |  |  | 0
| a)Size 60 x 60cm. Depth not exceeding 100cm | No. | 30 |  | 0
| b)Size 80 x 80cm. Depth not exceeding 150cm | No. | 24 |  | 0
| c)Size 100 x 100cm. Depth not exceeding 180cm | No. | 15 |  | 0
9.8.10 | 50m3 SEPTIC TANK |  |  |  | 0
| Construct effective volume 50 m3 Septic Tank out of reinforeced concrete wall on a base of 200mm thick R.C concrete bottom slab, RC top & bottom slab and reinforced concrete manhole cover. The work shall be carried out in accordance with the given sanitary and structural drawings & instructions. Price shall include excavation to the required depth, backfilling, cart away, internall wall water proofing and all the necessary assistance and incidental works. It is highly adviseable to refer the drawing during price fixing | No. | 1 |  | 0
9.8.12 | DILUTION & NEUTRALIZATION PIT |  |  |  | 0
| Construct effective volume 1.0m3 dilution & neutralization pit out of reinforced concrete shear wall on a base of 200mm thick R.C concrete bottom slab, RC top & bottom slab and reinforced concrete manhole cover. The work shall be carried out in accordance with the given sanitary and structural drawings & instructions. Price shall include excavation to the required depth, backfilling, cart away, wate proofing and all the necessary assistance and incidental works. | No. | 1 |  | 0
9.8.13 | Supply and lay storm water concrete pipes of half diameter 40cm with a minimum slope of 2% or natural ground slope which ever is greater on and including a firm bed of red ash 100mm thick below. The joints shall be grouted in cement sand mortar of (1:3). Price shall include 15cm thick stone masonry shoulder, excavation, cart away and all civil assistance works and grill cover with dia. 14cm rebar cover at 50mm spacing welded on flat frames and all other necessary accessories. | ml | 244 |  | 0
9.8.14 | Ditto as item No 9.8.13 but dia. 24 mm rebar grill cover welded to 5 mm thick and 50mm wide angle iron with all accessories as per the given detail drawing. The welding shall be done on best quality welding electrode and the rebar spacing shall be 50mm c/c. | ml | 15 |  | 0
9.8.15 | Ditto as item No 8.8.13 but dia. 600mm reinforced closed conduit pipe.. | ml | 6 |  | 0
Total Carried to Summary |  |  |  |  | 0
10, ELECTRICAL INSTALLATION WORKS:
SUPPLY, INSTALL, TEST & COMMISSION AN OVERALL SYSTEMS
10.1 | Distribution boards
1.01 | Floor Standing Central Main Distribution board CMDB (locate in Power/Genset House), with lockable door, Steel made enclosure, phase and neutral copper bus bars, Earthing lead, connectors, labling and all necessary accessories consisting of: (all Breakers are to be of type Legrand ,ABB or approved equivalents)
1 pc main MCCB of 800/1000A 3ph, Motorized
1 pc MCCB of 200A 3ph,
1 pc MCCB of 125A 3ph
1 pc MCCB of 80A 3ph
3 pcs MCCB of 63A 3ph
6 pcs MCCB of 50A 3ph
2 pcs MCB of 32A 3ph
3 pcs signal lamps (L1 - L2 - L3)
1 pc Voltmeter (0-500V) with selector switch
3 pcs Ammeter (0-600A) with transformer
1 pc Active Load/Power meter
| 1 pc Frequency meter |  |  |  | 0
| complete with bus bar system of 1600A and 25% reserve space. | Pcs | 1 |  | 0
1.02 | Wall surface mount Main Distribution board MDB-B2, with lockable door, Steel made enclosure, phase and neutral copper bus bars, Earthing lead, connectors, labling and all necessary accessories consisting of: (all Breakers are to be of type Legrand ,ABB or approved equivalents) |  |  |  | 0
| 1 pc MCCB of 63A 3ph, main, |  |  |  | 0
| 2 pcs MCB of 25A 3ph |  |  |  | 0
| 1 pc MCB of 20A 3ph |  |  |  | 0
| 1 pc MCB of 16A 1ph |  |  |  | 0
| 12 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 125A and 25% reserve space. | PCs | 1 |  | 0
1.03 | Wall surface mount Main Distribution board MDB-B1, with lockable door, Steel made enclosure, phase and neutral copper bus bars, Earthing lead, connectors, labling and all necessary accessories consisting of: (all Breakers are to be of type Legrand ,ABB or approved equivalents) |  |  |  | 0
| 1 pc MCCB of 50A 3ph, main, |  |  |  | 0
| 2 pcs MCB of 20A 3ph |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 3 pcs MCB of 16A 1ph |  |  |  | 0
| 9 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 100A and 25% reserve space. | PCs | 1 |  | 0
1.04 | Wall surface mount Main Distribution Board MDB-GF, with lockable door, Steel made enclosure, phase and neutral copper bus bars, Earthing lead, connectors, labling and all necessary accessories consisting of: (all Breakers are to be of type Legrand ,ABB or approved equivalents) |  |  |  | 0
| 1 pc MCCB of 63A 3ph, main |  |  |  | 0
| 2 pcs MCB of 25A 3ph |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 3 pcs MCB of 16A 1ph |  |  |  | 0
| 12 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 125A and 25% reserve space. | PCs | 1 |  | 0
1.05 | Ditto as 1.04 above, but MDB-1F and consisting of : |  |  |  | 0
| 1 pc MCCB of 63A 3ph, main |  |  |  | 0
| 1 pc MCB of 32A 3ph |  |  |  | 0
| 1 pc MCB of 25A 3ph |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 3 pcs MCB of 16A 1ph |  |  |  | 0
| 11 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 125A and 25% reserve space. | PCs | 1 |  | 0
1.06 | Ditto as 1.04 above, but MDB-2F and consisting of : |  |  |  | 0
| 1 pc MCCB of 80A 3ph, main |  |  |  | 0
| 3 pcs MCB of 25A 3ph |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 2 pcs MCB of 16A 1ph |  |  |  | 0
| 11 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 160A and 25% reserve space. | PCs | 1 |  | 0
1.07 | Ditto as 1.04 above, but MDB-3F and consisting of : |  |  |  | 0
| 1 pc MCCB of 125A 3ph, main |  |  |  | 0
| 1 pc MCB of 50A 3ph |  |  |  | 0
| 1 pc MCB of 32A 3ph |  |  |  | 0
| 1 pc MCB of 25A 3ph |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 6 pcs MCB of 16A 1ph |  |  |  | 0
| 6 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 200A and 25% reserve space. | PCs | 1 |  | 0
1.08 | Ditto as 1.04 above, but MDB-4F:8F and consisting of : |  |  |  | 0
| 1 pc MCCB of 50A 3ph, main |  |  |  | 0
| 1 pc MCB of 25A 3ph |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 6 pcs MCB of 16A 1ph |  |  |  | 0
| 8 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 100A and 25% reserve space. | PCs | 5 |  | 0
1.09 | Ditto as 1.04 above, but MDB-9F and consisting of : |  |  |  | 0
| 1 pc MCCB of 200A 3ph, main |  |  |  | 0
| 2 pcs MCB of 63A 3ph |  |  |  | 0
| 1 pc MCB of 40A 3ph |  |  |  | 0
| 1 pc MCB of 25A 3ph |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 2 pcs MCB of 16A 1ph |  |  |  | 0
| 3 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 400A and 25% reserve space. | PCs | 1 |  | 0
1.1 | Flush mount Sub-Distribution Board, SDB-B2.1/2, with lockable door, Steel made enclosure, phase and neutral copper bars, Earthing lead, connectors, labling and all necessary accessories consisting of: (all Breakers are to be of type Legrand ,ABB or approved equivalents) |  |  |  | 0
| 1 pc MCCB of 25A 3ph, main |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 6 pcs MCB of 16A 1ph |  |  |  | 0
| 6 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 50A and 25% reserve space. | PCs | 2 |  | 0
1.11 | Ditto as 1.10 above, but SDB-B1.1/2 and consisting of : |  |  |  | 0
| 1 pc MCCB of 20A 3ph, main |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 3 pcs MCB of 16A 1ph |  |  |  | 0
| 9 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 40A and 25% reserve space. | PCs | 2 |  | 0
1.12 | Ditto as 1.10 above, but SDB-GF1.1 and consisting of : |  |  |  | 0
| 1 pc MCCB of 25A 3ph, main |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 6 pcs MCB of 16A 1ph |  |  |  | 0
| 7 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 50A and 25% reserve space. | PCs | 1 |  | 0
1.13 | Ditto as 1.10 above, but SDB-GF1.2 and consisting of : |  |  |  | 0
| 1 pc MCCB of 25A 3ph, main |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 5 pcs MCB of 16A 1ph |  |  |  | 0
| 9 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 50A and 25% reserve space. | PCs | 1 |  | 0
1.14 | Ditto as 1.10 above, but SDB-F1.1 and consisting of : |  |  |  | 0
| 1 pc MCCB of 25A 3ph, main |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 6 pcs MCB of 16A 1ph |  |  |  | 0
| 6 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 50A and 25% reserve space. | PCs | 1 |  | 0
1.15 | Ditto as 1.10 above, but SDB-F1.2 and consisting of : |  |  |  | 0
| 1 pc MCCB of 32A 3ph, main |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 6 pcs MCB of 16A 1ph |  |  |  | 0
| 8 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 63A and 25% reserve space. | PCs | 1 |  | 0
1.16 | Ditto as 1.10 above, but SDB-F2.1 and consisting of : |  |  |  | 0
| 1 pc MCCB of 25A 3ph, main |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 6 pcs MCB of 16A 1ph |  |  |  | 0
| 6 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 50A and 25% reserve space. | PCs | 1 |  | 0
1.17 | Ditto as 1.10 above, but SDB-F2.2/3 and consisting of : |  |  |  | 0
| 1 pc MCCB of 25A 3ph, main |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 5 pcs MCB of 16A 1ph |  |  |  | 0
| 8 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 50A and 25% reserve space. | PCs | 2 |  | 0
1.18 | Ditto as 1.10 above, but SDB-F3.1 and consisting of : |  |  |  | 0
| 1 pc MCCB of 32A 3ph, main |  |  |  | 0
| 2 pcs MCB of 20A 1ph |  |  |  | 0
| 6 pcs MCB of 16A 1ph |  |  |  | 0
| 7 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 63A and 25% reserve space. | PCs | 1 |  | 0
1.19 | Ditto as 1.10 above, but SDB-F3.2 and consisting of : |  |  |  | 0
| 1 pc MCCB of 25A 3ph, main |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 7 pcs MCB of 16A 1ph |  |  |  | 0
| 7 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 50A and 25% reserve space. | PCs | 1 |  | 0
1.2 | Ditto as 1.10 above, but SDB-F3.3 and consisting of : |  |  |  | 0
| 1 pc MCCB of 50A 3ph, main |  |  |  | 0
| 1 pc MCB of 32A 3ph |  |  |  | 0
| 5 pcs MCB of 16A 1ph |  |  |  | 0
| 8 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 100A and 25% reserve space. | PCs | 1 |  | 0
1.21 | Ditto as 1.10 above, but SDB-F4:8 and consisting of : |  |  |  | 0
| 1 pc MCCB of 25A 3ph, main |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 6 pcs MCB of 16A 1ph |  |  |  | 0
| 6 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 50A and 25% reserve space. | PCs | 5 |  | 0
1.22 | Ditto as 1.10 above, but SDB-F9.1 and consisting of : |  |  |  | 0
| 1 pc MCCB of 25A 3ph, main |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 6 pcs MCB of 16A 1ph |  |  |  | 0
| 6 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 50A and 25% reserve space. | PCs | 1 |  | 0
1.23 | Ditto as 1.10 above, but SDB-F9.1/Kit and consisting of : |  |  |  | 0
| 1 pc MCCB of 40A 3ph, main |  |  |  | 0
| 1 pc MCB of 20A 3ph |  |  |  | 0
| 1 pc MCB of 25A 1ph |  |  |  | 0
| 1 pc MCB of 20A 1ph |  |  |  | 0
| 6 pcs MCB of 16A 1ph |  |  |  | 0
| 3 pcs MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 80A and 25% reserve space. | PCs | 1 |  | 0
1.24 | Ditto as 1.10 above, but SDB-F3.3/Lift and consisting of : |  |  |  | 0
| 1 pc MCCB of 32A 3ph, main |  |  |  | 0
| 1 pc MCB of 25A 3ph |  |  |  | 0
| 1 pc MCB of 16A 1ph |  |  |  | 0
| 1 pc MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 63A and 25% reserve space. | PCs | 1 |  | 0
1.25 | Ditto as 1.10 above, but SDB-F9/Lift and consisting of : |  |  |  | 0
| 1 pc MCCB of 63A 3ph, main |  |  |  | 0
| 1 pc MCB of 50A 3ph |  |  |  | 0
| 1 pc MCB of 16A 1ph |  |  |  | 0
| 1 pc MCB of 10A 1ph |  |  |  | 0
| complete with bus bar system of 125A and 25% reserve space. | PCs | 2 |  | 0
1.26 | Ditto as 1.10 above, but SDB-WPS & consisting of |  |  |  | 0
| 1 pc main MCCB of 32A 3ph |  |  |  | 0
| 1 pc MCB of 20A 3ph |  |  |  | 0
| 1 pc MCB of 16A 3ph |  |  |  | 0
| 1 pc MCB of 10A 3ph |  |  |  | 0
| complete with bus bar system of 63A and 25% reserve space. | PCs | 1 |  | 0
1.27 | Ditto as 1.10 above, but SDB-Em & consisting of |  |  |  | 0
| 1 pc main MCCB of 32A 3ph |  |  |  | 0
| 1 pc MCB of 20A 3ph |  |  |  | 0
| 1 pc MCB of 16A 3ph |  |  |  | 0
| 1 pc MCB of 10A 3ph |  |  |  | 0
| complete with bus bar system of 63A and 25% reserve space. | PCs | 2 |  | 0
1.28 | Flush mount Uninterupted Power supply system (UPS), MDB-UPS, with lockable door, Steel made enclosure, phase and neutral copper bars, Earthing lead, connectors, labling and all necessary accessories consisting of: |  |  |  | 0
| 1 pc MCCB of 100A 3ph - main |  |  |  | 0
| 1 pc MCB of 50A 3ph |  |  |  | 0
| 1 pc MCB of 32A 3ph |  |  |  | 0
| 1 pc MCB of 20A, 1ph |  |  |  | 0
| 1 pc MCB of 16A, 1ph |  |  |  | 0
| 1 pc MCB of 10A, 1ph |  |  |  | 0
| and complete with bus bar system of 200A and 25% reserve space. | PCs | 1 |  | 0
10.2 | Light points (Wire to be complied with industry standard or approved equivalent) |  |  |  | 0
2.01 | Light points fed through PVC sheathed copper conductor of 2x2.5 sqmm in thermoplastic conduit of dia.13mm in/under surface including Junction boxes with covers, screw type connectors, insulating caps and all necessary accessories. | PCs | 3214 |  | 0
10.3 | Recessed/Flush mount ON-OFF Switches LEGRAND, SUNO types or approved equivalent with appropriate cover plate, scattola and accessories. |  |  |  | 0
3.01 | Single-pole switch (774001+774041) | Pcs | 75 |  | 0
3.02 | Water proof Single-pole switch (Legrand Nepteo 686760) | Pcs | 120 |  | 0
3.03 | Double-pole switch (774005+774041) | Pcs | 199 |  | 0
3.04 | Water proof Double-pole switch (Legrand Nepteo 686763) | Pcs | 28 |  | 0
3.05 | Two-Way switch (774006+774041) | Pcs | 210 |  | 0
3.06 | Double-pole Two-Way switch (774008+774041) | Pcs | 30 |  | 0
3.07 | Intermediate switch (774007+774041) | Pcs | 36 |  | 0
3.08 | Triple-pole switch (774005+774001+774042) | Pcs | 33 |  | 0
10.4 | Socket and Power Outlet points (Wire to be complied with industry standard or approved equivalent) |  |  |  | 0
4.01 | Socket outlet points in regid thermoplastic conduit of diameter 16mm fed by pvc conductor of 3x2.5mm2 | Pcs | 323 |  | 0
4.02 | Ditto as 4.01 but for water heaters | Pcs | 8 |  | 0
4.03 | Ditto as 4.01 but for twin socket outlets | Pcs | 198 |  | 0
4.04 | Power outlet points, cable of 3x2.5mm2 in rigid pvc conduit of dia 16mm. | Pcs | 4 |  | 0
4.05 | Power outlet points, cable of 3x4mm2 in rigid pvc conduit of dia 21mm. | Pcs | 10 |  | 0
4.06 | Power outlet points, cable of 3x6mm2 in rigid pvc conduit of dia 25mm. | Pcs | 4 |  | 0
4.07 | Power outlet points, cable of 4x4mm2 in rigid pvc conduit of dia 32mm. | Pcs | 4 |  | 0
4.08 | Power outlet points, cable of 4x6mm2 in rigid pvc conduit of dia 40mm. | Pcs | 4 |  | 0
4.09 | Floor reccessed socket outlet points, fed by pvc conductor of 3x2.5mm2 in rigid pvc conduit of dia 21mm. | Pcs | 36 |  | 0
10.5 | Recessed/Flush mount Socket/Power Outlets LEGRAND, SUNO types or approved equivalent with P+N+E terminals, appropriate cover plate, scattola and all accessories. |  |  |  | 0
5.01 | Socket outlet (774023), 16A/1ph. | Pcs | 323 |  | 0
5.02 | Ditto as 5.01 above but twin socket outlet 2(774020)+774042 | Pcs | 198 |  | 0
5.03 | Power outlet industry standard type Legrand of 16A/1ph. | Pcs | 4 |  | 0
5.04 | Ditto as 5.03 above but for heater with light indicator & switch | Pcs | 8 |  | 0
5.05 | Ditto as 5.03 above but of 20A/1ph, | Pcs | 10 |  | 0
5.06 | Ditto as 5.03 above but of 25A/1ph, | Pcs | 4 |  | 0
5.07 | Ditto as 5.03 above but of 20A/3ph, | Pcs | 4 |  | 0
5.08 | Ditto as 5.03 above but of 25/32A/3ph, | Pcs | 4 |  | 0
5.09 | Floor mount/reccessed type outlets with enclosure & openable cover of 4[16A/1ph,] | Pcs | 36 |  | 0
10.8 | Supply, install and test the specified type of Light Fittings with Lamps (or approved equivalents) |  |  |  | 0
8.01 | 1-LED PANEL Light, NPNLED 4515/58w/126 SMD LED with 58w LED Lamp | No. | 147 |  | 0
8.02 | 2-Industrial Light, NLED492N SMD LED with 40w LED Lamp [sealed clips IP65 water-proof batten] | No. | 674 |  | 0
8.03 | 3-LED PANEL Light, NPNLED 4514/43w/66 SMD LED with 43w LED Lamp | No. | 854 |  | 0
8.04 | 4-LED PANEL Light, NPNLED 4514/37w/66 SMD LED with 37w LED Lamp | No. | 258 |  | 0
8.05 | 5-LED PANEL Light, NPNLED 4513/37w/123 SMD LED with 37w LED Lamp | No. | 129 |  | 0
8.06 | 6-LED panel Lightings, YLA214P-L with 24w LED Lamp | No. | 58 |  | 0
8.07 | 7-Ceil-Surfaced Lightings,YSD-02A/01B with 18w LED Lamp | PCs | 70 |  | 0
8.08 | 8-Down Light, NLED 9185M SMD LED with 9/12w LED Lamp | PCs | 112 |  | 0
8.09 | 9-Wall surface Lightings, SPECTO 899010 with 1x18w, T8/G13 Prismatic Lamp | PCs | 20 |  | 0
8.1 | 10-Wall-Surface Light, NWM355R SMD LED with 18w LED Lamp | No. | 20 |  | 0
8.11 | E-Modus HELIOS LED OZAWHEL3 SA PT LED 96cd 3 hours (Emergency Lightings) | No. | 24 |  | 0
8.12 | PORTAL "EXIT" Lighting, 899751, with 1x11w TC-5/G23 OPAL VVG E/G-1 Lamp | No. | 48 |  | 0
8.13 | Spot Light, NLED 9185M SMD LED with 7w LED Lamp | No. | 220 |  | 0
8.14 | Double Spot Light, NLED 9185M SMD LED with 7w LED Lamp | No. | 130 |  | 0
8.15 | Aluminum Light, NLED 9185M SMD LED | Ml | 330 |  | 0
8.16 | Magnatic Light NLED 9185M SMD LED | Ml | 100 |  | 0
8.17 | Pendant NLED 9185M SMD 58w LED Lamp | No. | 8 |  | 0
10.9 | Power Cables(XLPE 0.6/KV or approved equ.) |  |  |  | 0
9.01 | 2[3x185/95+1x195mm2] (EEPCO/Genset to KWHM to ATS, & ATS to CMDB) | MtL | 100 |  | 0
9.02 | 3x95/50+1x50mm2 | MtL | 90 |  | 0
9.03 | 3x70/35+1x35mm2 | MtL | 40 |  | 0
9.04 | 3x50/25+1x25mm2 | MtL | 40 |  | 0
9.05 | 3x35/16+1x16mm2 | MtL | 60 |  | 0
9.06 | 3x25/16+1x16mm2 | MtL | 60 |  | 0
9.07 | 5x16mm2 | MtL | 60 |  | 0
9.08 | 5x10mm2 | MtL | 680 |  | 0
9.09 | 5x6mm2 | MtL | 1110 |  | 0
9.1 | 5x4mm2 | MtL | 100 |  | 0
9.11 | 3x6mm2 | MtL | 80 |  | 0
9.12 | 3x4mm2 | MtL | 60 |  | 0
10.1 | Cable way and Manhole
10.01 | Rigid pvc pipe of dia.110mm | MtL | 100 |  | 0
10.02 | Rigid pvc pipe of dia.70mm | MtL | 200 |  | 0
10.03 | Rigid pvc pipe of dia.50mm | MtL | 500 |  | 0
10.04 | Rigid pvc pipe of dia.40mm | MtL | 400 |  | 0
10.05 | Rigid pvc pipe of dia.32mm | MtL | 300 |  | 0
10.06 | Rigid pvc pipe of dia.25mm | MtL | 200 |  | 0
10.09 | Stainless steel vertical Cable ladder of 500x70mm for low volatge power complete with all connecting and fixing accessories | MtL | 80 |  | 0
10.1 | Stainless steel horizontal Cable tray of 300x70mm for power & low voltage from CMDB to each duct & interconnecting b/n ducts complete with all connecting and fixing accessories | MtL | 60 |  | 0
10.11 | Concrete Manhole 500x500x600mm with removable concrete cover as shown on the drawing | No | 4 |  | 0
10.12 | Concrete Manhole 600x600x800mm with removable concrete cover as shown on the drawing | No | 4 |  | 0
10.13 | Concrete Manhole 800x800x1000mm with removable concrete cover as shown on the drawing | No | 1 |  | 0
10.11 | Lightening Prevention system
11.1 | Lightening Preventor Type SI60 to be installed as per the drawing with all necessary fixing, Connecting and clamping accessaries and 4mt Almunium mast (Almunium mast should be supported at three directions) with related & proper signal light-lamp | LS | 1 |  | 0
11.2 | 1x50mm2 bare copper horizontal conductor run along top-roof beams/surface | MtL | 100 |  | 0
11.3 | 1x25mm2 bare copper down conductor run in PVC conduit of diam 32mm | MtL | 50 |  | 0
11.4 | Earthing rod of 16x2400mm to be driven in earthing pit of 500x500x600mm(resistance R < 5 ohm) | Pcs | 1 |  | 0
11.5 | Lightening Event counter to be mounted at 1.6mt above NGL | Pcs | 1 |  | 0
10.12 | Low Voltage Earthing system |  |  |  | 0
12.1 | Copper Earthing rod of 16x2400mm to be driven to earth with Earthing pit of 600x600x800mm | Pcs | 3 |  | 0
12.2 | Copper conductor of 2(1x95mm2) for Earthing | MtL | 60 |  | 0
12.3 | Equipotential bonding bar of 100x25mm copper bar to be mounted inside power room as shown | No | 1 |  | 0
10.2 | COMPACT TRANSFORMER: - Supply, Install/assemble, Test and Commission) |  |  |  | 0
20.1 | EEPCO Standard Compact type Transformer of 15KV, 630KVA, 400/230Vac with Switch gears, energy meter, concrete seat pad, concret poles, related cables & etc, including all necessary items & accessories. | Set | 1 |  | 0
10.21 | Stand-By Diesel Engine Power Genrator Set: - (Supply, Install/assemble, Test and Commission) |  |  |  | 0
21.1 | Stand-by seilent and canopy type Diesel engine power Genrator set of industry standard or approved equivalent types with capacity 500KVA/400KWp, complete with compatible Automatic Transfer Switch (ATS), designed to operate at 400/230Vac, 50HZ frequency, 1500RPM, fuel transfer pump inside, etc and with all necessary items and accessoies (refer technical details). The contract price also includes all required civil works as per the drawing. | Set | 1 |  | 0
| Total carried to Summary |  |  |  | 0
11, DATA NETWORK SYSTEM WORKS:
1 | Data System
Supply, installation, testing, and commissioning of a complete ICT and network infrastructure system, including server room equipment, structured cabling, network switching, wireless connectivity, security systems, and supporting power and cooling infrastructure. The works shall include provision of network cabinets, enterprise firewall, enterprise router, rack-mounted server, managed network switches, patch panels, cable management accessories, Cat 6 UTP cabling, RJ45 outlets, connectors, trunking, wireless access points, UPS systems, precision air conditioning for server rooms, and IP-based CCTV surveillance system. The contractor shall provide all materials, accessories, mounting hardware, labeling, testing, configuration, documentation, and commissioning necessary for a fully operational system. All installations shall comply with structured cabling standards, manufacturer recommendations, and applicable ICT infrastructure standards, ensuring reliable, secure, and scalable network connectivity for the facility.
1.1 | 42U Network Cabinet with ventilation, lockable door, cable management, and space for patch panels and switches. | PCs | 2 |  | 0
1.2 | Firewall with advanced security features, including stateful and deep packet inspection, intrusion prevention, and VPN support, capable of filtering up to 1 Gbps of traffic. Configured for network protection and integration with the existing Cat 6 UTP cabling system, along with proper labeling. | PCs | 2 |  | 0
1.3 | Enterprise-Grade Router (Multi-WAN, Gigabit, VPN, Firewall) Supply, install, configure, test and commission enterprise-grade router with minimum 2× Gigabit WAN ports and 4× Gigabit LAN ports, supporting Multi-WAN load balancing and failover, advanced routing (Static/RIP/OSPF), VLAN (802.1Q), NAT, DHCP, integrated stateful packet inspection firewall, and VPN (IPSec/L2TP/OpenVPN) for secure site-to-site and remote access connectivity, including all required accessories and configuration. | PCs | 2 |  | 0
1.4 | High-performance rack-mounted server with dual processors, 64GB RAM, 2TB SSD storage, RAID controller, and hot-swappable power supply. Suitable for hosting applications, databases, or virtualization. | PCs | 1 |  | 0
1.5 | 48-port patch panel for Cat 6 cables, including labeling for organized cable management, along with Cat 6 UTP cable and Rack mounted. | PCs | 2 |  | 0
1.6 | Managed Gigabit Ethernet switch with 48 ports, Rack mounted, supporting high-speed data transmission and VLAN configurations. | PCs | 2 |  | 0
1.7 | Precision air conditioning unit (PAC) designed for server rooms, 1.5-ton capacity, energy-efficient, and capable of maintaining temperature and humidity levels for optimal equipment operation. | PCs | 1 |  | 0
1.8 | 2kVA Uninterruptible Power Supply with pure sine wave output, automatic voltage regulation (AVR), and at least 15 minutes of backup time at full load. Essential for protecting critical server room equipment. | PCs | 1 |  | 0
1.9 | IP-based indoor security camera with 1080p resolution, PoE support, night vision, motion detection, and remote monitoring capabilities for securing the server room. | PCs | 2 |  | 0
1.10 | Cable Management Panels: Panels for managing and organizing patch cords within the network cabinet, compatible with 42U rack. | PCs | 2 |  | 0
1.11 | 9U Wall Mount Network Cabinet with ventilation, lockable door, cable management, and space for patch panels and switches. | PCs | 12 |  | 0
1.12 | 6U Wall Mount Network Cabinet with ventilation, lockable door, cable management, and space for patch panels and switches. | PCs | 18 |  | 0
1.13 | Dual-band access points for Wi-Fi coverage, supporting 802.11ac or newer standards for high-speed wireless connectivity. | PCs | 12 |  | 0
1.14 | 24-port patch panel for Cat 6 cables, including labeling for organized cable management, along with Cat 6 UTP cable and conduit installation for switch connectivity. | PCs | 28 |  | 0
1.15 | Managed Gigabit Ethernet switch with 24 ports, supporting high-speed data transmission and VLAN configurations. | PCs | 28 |  | 0
1.16 | Category 6 (Cat 6) UTP Ethernet cable, 305-meter roll, tested for gigabit speeds and suitable for structured cabling within the server room and end devices. | Roll | 35 |  | 0
1.17 | RJ45 connectors compatible with Cat 6 cables, designed for secure and efficient terminations in patch panels and wall outlets. (200 connectors) | Pack | 5 |  | 0
1.18 | Network Cable Trunking Sizes 40x25mm 3m PVC Trunking With Holes | PCs | 1000 |  | 0
1.19 | Dual-port RJ45 outlet with faceplate, designed for Cat 6 cable termination, including Cat 6 UTP cable and conduit installation. | PCs | 60 |  | 0
1.20 | Dual-port outlet supporting RJ45 (Cat 6 data) and RJ11 (telephone) connections with faceplate, mounting box, and including Cat 6 UTP cable and conduit installation. | PCs | 90 |  | 0
1.21 | Single-port RJ45 outlet with faceplate, designed for Cat 6 cable termination, including Cat 6 UTP cable and conduit installation. | PCs | 160 |  | 0
1.22 | Supply, installation, configuration, and commissioning of an IP-based indoor CCTV surveillance system consisting of 8 PoE-supported 1080p IP cameras (with night vision, motion detection, and remote monitoring), including all mounting accessories, Cat6 UTP cabling with terminations, conduits/trunking, PoE network switch, NVR with suitable storage capacity for 30-day recording, RJ45 connectors, patch panel, UPS backup, testing, labeling, documentation, and a 55-inch LED display monitor (including HDMI/VGA cable, keyboard, and mouse) for local control and monitoring — complete in all respects. | PCs | 30 |  | 0
2 | TVRO system points and outlets (Provision to be as per industry standards with all compatible accessories)
2.1 | TV point fed through co-axial cable of RG/59 BU inside PVC conduit of 25mm diameter including junction boxes with covers, insulating screw cap connectors, (High-quality coaxial cable for TV installations, suitable for video signal transmission.) | PCs | 12 |  | 0
2.2 | Flush mounted TVRO outlets type Legrand Suno (TV-R-SAT) | PCs | 12 |  | 0
2.3 | TVRO Splitter connection box of 150x100x70mm with cover. | PCs | 4 |  | 0
| Total Sum |  |  |  | 0
12, ELECTRO MECHANICAL WORKS:
General Note:- All HVAC components like AHU, CHILLER and terminal units shall comply with EBCS11 and ASHRAE standards. All Duct sytems shall be pressure tested and approved.
1 | AIR HANDLING UNIT WITH ALL ACCESSORIES.
Supply, fix,test and commission multi section air handling units /AHU/ as per the manufacturer's specification & instruction,including valves,short length piping & fittings,instrumentation devices & supports all as specified in the standared manufacturer's specification and/or shown on the drawings & equipment schedule.
Unit price shall include the following accessories on all AHU's chilled water pipe connection as detailed on the dwg's.
Ground mounted air handling unit & it shall be :
- From dual-layered adiabatic panel
- Factory assembled units and acc's
- Cooling /Air cooled/ coil
- Draw though air supply fan
-Panel type filters/washable/
The unit shall also include necessary thermostats, pressure gauges and hinged access panel doors.
The contractor shall verify total external static pressure of the supply fan,depending on the type of air diffuser, filters,sound dampers and duct layout modification which might be done on site.
Indoor design condition - 18 - 23ºC
Relative humidity 30 - 60% RH
Cooling water inlet/outlet temperature - 7 / 12ºC
A) AHU- (DATA CENTER)
| Supply air =1200lit/sec | No | 1 |  | 0
Ext.static pressure=………….
Cooling capacity=40kw
Type ……
Model…….to be confirmed
B ) Air cooled chiller (With all piping works & accessories required)
| Model…….to be confirmed | No
Chilled Water Temp (In/Out) 7 °C / 12 °C
Indoor Design Temp 18–23 °C
| Relative Humidity 30–60% RH |  | 1 |  | 0
Supply Air Volume 1,200 L/s (~4,320 m³/h)
Recommended Chiller Capacity 45–55 kW (with 10–30% margin)
Certifications required : ISO 9001 – Quality Management System Ensures consistent product quality and manufacturing standards. ISO 14001 – Environmental Management System Confirms the manufacturer’s commitment to sustainable practices. AHRI Certification (ACCL Program)
2 | Galvanised steel duct work
2.1 | Supply air duct
| Galvanized Steel Duct Duct 1 mm thickness | m2 | 7800 |  | 0
| Galvanized Steel Duct Duct 0.8 mm thickness | m2 | 7500 |  | 0
| Galvanized Steel Duct Duct 0.6 mm thickness | m2 | 6900 |  | 0
2.2 | Return air duct |  |  |  | 0
| Galvanized Steel Duct Duct 1 mm thickness | m2 | 7800 |  | 0
| Galvanized Steel Duct Duct 0.8 mm thickness | m2 | 7500 |  | 0
| Galvanized Steel Duct Duct 0.6 mm thickness | m2 | 6900 |  | 0
3 | Supply Air & Extracting fans accessories |  |  |  | 0
3.1 | Air extracting fans & accessories for Basement parking |  |  |  | 0
Included accessories (to be priced as part of the item):. Duct-mounted silencer: One silencer mounted on the suction side of each fan. Silencer to be sized to achieve noise levels specified on drawings or in the project specification. Mounting feet and supports: Mounting feet, supports, hangers, vibration isolation as required. Control systems: All necessary control systems for fan operation, including starters, speed control (if applicable), interlocks, and interfaces to BMS or local control panels as specified. Other accessories: Flexible connectors, flanges, gaskets, access doors (where required) and any other items required to complete the system as a fully operational installation. Standards and compliance: Fire safety: Fan and accessories shall comply with all recognized and approved fire safety standards applicable to car parks and smoke extraction systems. Manufacturer’s instructions: All equipment shall be installed strictly in accordance with the manufacturer’s recommendations and installation manuals.
| a) EX-1(Parking) | No | 5 |  | 0
i) Fan Capacity
Type :……. DYN AIR or equivalent
Model …..To be confirmed
Capacity : Extract air =2500 liter/second
Exter. Static pressure =200Pa
| ii) Supply and install Europe manufactured /standard filter (washable) . Q = 2500 liter/second | No | 5 |  | 0
| b) EX-2(Data center) | No | 1 |  | 0
i) Fan Capacity
Type :…….CENTRIFUGAL
Model ….. To be confirmed
Capacity : Extract air =1200 liter/second
Exter. Static pressure =500Pa
| ii) Supply and install Europe manufactured /standard filter (washable) . Q = 1200 liter/second | No | 1 |  | 0
3.2 | Roof mounted Air Supply fan & accessories for |  |  |  | 0
| a)SP-1 | No | 1 |  | 0
i) Fan Capacity
Type :……. DYN AIR or equivalent
Model ….. To be confirmed
Capacity : Supply air =2100 liter/second
Exter. Static pressure =
| b)SP-2 | No | 1 |  | 0
i) Fan Capacity
Type :……. DYN AIR or equivalent
Model …..To be confirmed
Capacity : Supply air =15000 liter/second
Exter. Static pressure =
4 | Supply air Grills / wall mouted Mounted/ |  |  |  | 0
| Supply, fix, test and commission supply air diffusers. The frame from high quality extruded aluminium profile and standard(20mm) blade spacing. Price shall include foam gasket seal around the back of the frame and flexible duct connectors as required. | No | 5 |  | 0
1) SAG-1
Capacity =420liter/sec
Size : 900x150mmxmm
Type : air master or equivalent
Model: ---
Colour: As per the Architect's preference
5 | Supply air Diffusers /Ceiling Mounted/
Supply, fix, test and commission supply air diffusers. The frame from high quality extruded aluminium profile and standard(20mm) blade spacing. Price shall include foam gasket seal around the back of the frame and flexible duct connectors as required.
| 1) SAD-1 | No | 6 |  | 0
Capacity =200liter/sec
Size : 300x300mmxmm
Type : air master or equivalent
Model: ----
Colour: As per the Architect's preference
6 | Return air GRILLES / Ceiling Mounted/
| Supply, fix, test and commission supply air diffusers. The frame from high quality extruded aluminium profile and standard(20mm) blade spacing. Price shall include foam gasket seal around the back of the frame and flexible duct connectors as required. |  |  |  | 0
| 1) RAG-1(for parking) | No | 2 |  | 0
Capacity =1250liter/sec
Size : 500x500mmxmm
Type : air master or equivalent
Model: ----
Colour: As per the Architect's preference
| 2) RAG-2(for datacenter) | No | 3 |  | 0
Capacity =400liter/sec
Size : 500x200mmxmm
Type : air master or equivalent
Model: ----
Colour: As per the Architect's preference
7 | JET FAN: Supply and install Compact, smart solutions for smoke extraction induction type jet fans with fire rating Up to 400°C/120 min (F400) Continuous medium temperature up to 45°C
7.1 | JET FAN |  |  |  | 0
| With: 0.5 m³/s(500lps)-Flow rate, 12 m/s-speed/jet velocity, 7.2 N thrust, 5:1 entrainment ratio, axial/Induction type (compact) | No | 6 |  | 0
7.2 | Variable frequency Drive(VFD)(For speed control based on CO sensors) | No | 3 |  | 0
8 | TOILET VENTILATION
8.1 | EXHAUST AIR FAN(at roof top serving ten floors) | pcs | 2 |  | 0
Supply, Install, test and commissining of Exhaust air fan as shown on the drawing. The price shall include all necessary accessories like flexible connection, control unit and all other necessary accessories for proper functioning of the system. Type: Centrifugal roof-mounted exhaust fan, vertical discharge, belt- or direct-driven Application: Toilet/odour exhaust riser serving multiple floors, continuous or intermittent operation Mounting: On roof curb with weatherproof housing, bird screen, and backdraft damper
Type: TWIN ROOF FAN
Airflow: ≥5,000 L/s (minimum at design point)
Total Pressure Loss: 450-600Pa
Type: TWIN ROOF FAN
Motor, power and electrical
(Indicative — final selection depends on fan curve and manufacturer.)
Estimated motor power: approx. 3–7.5 kW (Check against fan performance data at 5,000 L/s @ selected ESP.)
Power supply: 400 V, 3-phase, 50 Hz (typical EU standard)
Motor protection:IP55 enclosure (minimum) ,Class F insulation
Speed control:
VFD (inverter) control recommended for balancing and energy savings
Controls: Equipped with Auto/manual selector switch
Certification / Approval
Approved Document F (UK) :Ventilation performance & building compliance
Ventilation Test Certificate :Confirms airflow meets regulations
Installer Competency (NICEIC) : Ensures proper installation & commissioning
CE Marking :Safety & compliance for equipment
AMCA Certification: Verified fan performance
ISO 9001 / 14001: Quality & environmental management
8.2 | Duct work: Supply, fix, test and commission galvanized steel air distribution ducts as where shown on the drawing. All duct construction and installation shall follow standards and recommendations given on SMACNA (Sheet Metal and Air Conditioning Contractors National Association, INC) and EBCS 11. Price shall include all the necessary duct reinforcement, fixing clamps to slabs, walls, vanes, etc and all the necessary fittings works on the drawing. All duct construction & installation shall follow the technical specification of this project, standardes and recommendations given.
| Galvanized Steel Duct Duct 1 mm thickness | m2 | 7800 |  | 0
| Galvanized Steel Duct Duct 0.8 mm thickness | m2 | 7500 |  | 0
| Galvanized Steel Duct Duct 0.6 mm thickness | m2 | 6900 |  | 0
8.3 | Air Outlets | pcs | 90 |  | 0
Supply and install Exhaust Grills grills (EAG) which is made from high quality extruded alluminium profile with 33mm flange width as shown on the drawing complete with plenium box , flexible duct and all fixing accessories.
Type: Air Master or Equivalent
Model: ARG
Colour: As per the Architect's preference
Size:
150x150
8.4 | Volume Control Damper | pcs | 90 |  | 0
Supply, fix, test and commission volume control dampers.The frame shall be constructed from galvanized steel sheet and coated with aluminium spray.Price shall include all the necessary accessories and connecting pieces.
Type: Air Master or Equivalent
Model: AVCD
Size: 125x125
9 | SPLIT Type Air Condition (AC) System (Indoor-Outdoor cool & heat units) - The unit shall comply with industry, ISO/IEC standards & recommendations://for Directorate offices// | No | 6
Supply, mount/fix, install and test wall mounted split type (indoor-outdoor unit) thermally & electrically operated automated AC /cool & heat/ units with switch & remot controler including each unit points fed through pvc insulated copper conductor sizes of 3x2.5mm2 inside PVC conduits of 16mm. diameter with all the required mounting and fitting accessories; with the following capacity of:- Capacity (air conditioner): 8000 Btu/h Power (watt): ~2,460 watt, 220-240 Vac, 50 hz. Air switch capacity: 16A, 1ph. Operating temprature range: -5 oc - +50 oc (for cooling & heating unit).
Features Specifications
Cooling/Heating Capacity 9,000 BTU (suitable for 200–300 sq ft)
Compressor Type Rotary or Inverter (for energy efficiency and quiet operation)
Refrigerant R-32 or R-410A (eco-friendly and efficient)
Energy Efficiency SEER ≥ 20 (Seasonal Energy Efficiency Ratio)
Heating Type Heat Pump (reversible cycle for year-round use)
Airflow ≥ 400 CFM (Cubic Feet per Minute)
Noise Level Indoor: ≤ 35 dB, Outdoor: ≤ 50 dB
Power Supply 220–240V, 50/60Hz, Single Phase
Smart Features WiFi control, programmable timer, auto restart
Filters Anti-bacterial, dust, and deodorizing filters
Standards & Compliance
ISO 15042:2017 – Performance testing and rating for multi-split systems
ISO 5151 – Non-ducted air conditioners and heat pumps
IEC 60335-2-40 – Electrical safety for AC units
Energy Efficiency: SEER ≥ 20 (where applicable)
10 | SPLIT Type Air Condition (AC) System
10.1 | SPLIT Type Air Condition (AC) System (Indoor-Outdoor cool & heat units) - The unit shall comply with industry, ISO/IEC standards & recommendations: | pc | 12 |  | 0
Supply, mount/fix, install and test wall mounted split type (indoor-outdoor unit) thermally & electrically operated automated AC /cool & heat/ units with switch & remot controler including each unit points fed through pvc insulated copper conductor sizes of 3x2.5mm2 inside PVC conduits of 16mm. diameter with all the required mounting and fitting accessories; with the following capacity of:- Capacity (air conditioner): 12,000 Btu/h Power (watt): ~2,460 watt, 220-240 Vac, 50 hz. Air switch capacity: 16A, 1ph. Operating temprature range: -5 oc - +50 oc (for cooling & heating unit).
Parameter Specification
Cooling/Heating Capacity 12,000 BTU/h
Power Consumption ~2,460 W,220–240 V AC, 50 Hz
Compressor Type Inverter rotary or scroll, hermetically sealed
Refrigerant R-32 or R-410A (non-ozone depleting)
Energy Efficiency SEER ≥ 20 (Seasonal Energy Efficiency Ratio)
Air Switch Rating 16 A, 1 Phase
Operating Temperature Range -5°C to +50°C
Airflow Rate ≥ 400 CFM
Noise Level Indoor ≤ 35 dB, ≤ 50 dB
Control Infrared remote with LCD display, optional WiFi/app control
Filters Washable anti-bacterial, dust, and deodorizing filters
Casing : re-retardant ABS (indoor), galvanized steel with anti-corrosion coating (outdoor)
Standards & Compliance
ISO 15042:2017 – Performance testing and rating for multi-split systems
ISO 5151 – Non-ducted air conditioners and heat pumps
IEC 60335-2-40 – Electrical safety for AC units
Energy Efficiency: SEER ≥ 20 (where applicable)
10.2 | A 24,000 BTU VRF /Multi-split type air conditioner system with one outdoor unit and three indoor units (Indoor-Outdoor cool & heat units) - The unit shall comply with industry, ISO/IEC standards & recommendations://for Reserchers & technical offices//Third floor+v.studio | pc | 2 |  | 0
Supply, mount/fix, install and test wall mounted multi-split type (indoor-outdoor unit) thermally & electrically operated automated AC /cool & heat/ units with switch & remot controler including each unit points fed through pvc insulated copper conductor sizes of 3x2.5mm2 inside PVC conduits of 16mm. diameter with all the required mounting and fitting accessories; with the following capacity of:- Capacity (air conditioner): Indoor 24000 Btu/h & Power (watt): ~2,460 watt, 220-240 Vac, 50 hz. Air switch capacity: 16A, 1ph. Operating temprature range: -5 oc - +50 oc (for cooling & heating unit).
Features of Outdoor Unit Specification
Cooling Capacity 24,000 BTU
Heating Capacity Up to 24,000 BTU
Compressor Inverter Rotary
Refrigerant R-410A
Max Connectable Capacity 24,000 BTU
Power Supply 208/230V, 1Ph, 60Hz
Noise Level ~55 dB(A)
Dimensions (W×D×H) 34.25" × 12.6" × 31.8"
Weight 130 lbs
Energy Efficiency High SEER, inverter tech
Features of Indoor Units (3 Units – Wall-Mounted) Specification
Cooling Capacity: 8,000 BTU per unit
Noise Level: As low as 19 dB(A)
Air Filtration: Multi-stage filters (dust, pollen, odors)
Smart Features: Wi-Fi control, app integration
Design: Slim profile, hidden display, quiet operation
Installation: Quick-mount system, flexible piping
Special Features
Volt Care : Protects against voltage fluctuations
Coating: Corrosion-resistant heat exchanger
GEN Mode: Operates at lower power levels for generator compatibility
Room-by-Room Control: Independent temperature settings for each zone
10.3 | A 24,000 BTU VRF/ Multi-split type air conditioner system with one outdoor unit and three indoor units (Indoor-Outdoor cool & heat units) - The unit shall comply with industry, ISO/IEC standards & recommendations://for ICT & technical staff | pc | 2 |  | 0
Supply, mount/fix, install and test wall mounted multi-split type (indoor-outdoor unit) thermally & electrically operated automated AC /cool & heat/ units with switch & remot controler including each unit points fed through pvc insulated copper conductor sizes of 3x2.5mm2 inside PVC conduits of 16mm. diameter with all the required mounting and fitting accessories; with the following capacity of:- Capacity (air conditioner): Indoor 24000 Btu/h & Power (watt): ~2,460 watt, 220-240 Vac, 50 hz. Air switch capacity: 16A, 1ph. Operating temprature range: -5 oc - +50 oc (for cooling & heating unit).
Features of Outdoor Unit Specification
Cooling Capacity 24,000 BTU
Heating Capacity Up to 24,000 BTU
Compressor Inverter Rotary
Refrigerant R-410A
Max Connectable Capacity 24,000 BTU
Power Supply 208/230V, 1Ph, 60Hz
Noise Level ~55 dB(A)
Dimensions (W×D×H) 34.25" × 12.6" × 31.8"
Weight 130 lbs(optional)
Energy Efficiency High SEER, inverter tech
Features of Indoor Units (2 Units – Wall-Mounted) Specification
Cooling Capacity: 12,000 BTU per unit
Noise Level: As low as 19 dB(A)
Air Filtration: Multi-stage filters (dust, pollen, odors)
Smart Features: Wi-Fi control, app integration
Design: Slim profile, hidden display, quiet operation
Installation: Quick-mount system, flexible piping
Special Features
Volt Care : Protects against voltage fluctuations
Coating: Corrosion-resistant heat exchanger
GEN Mode: Operates at lower power levels for generator compatibility
Room-by-Room Control: Independent temperature settings for each zone
Controls: Central VRF controller + individual room controllers; BMS/Modbus gateway optional.
Power: Dedicated supply to outdoor; control/power to BS box and indoors per manufacturer.
Condensate: Gravity drain or pumps per unit to nearest drain points.
10.4 | A 12,000 BTU VRF/Multi-split type air conditioner system with one outdoor unit and two indoor units (Indoor-Outdoor cool & heat units) - The unit shall comply with industry, ISO/IEC standards & recommendations://for Library,EOC+Audio,PHEOC// | pc | 3 |  | 0
Supply, mount/fix, install and test wall mounted multi-split type (indoor-outdoor unit) thermally & electrically operated automated AC /cool & heat/ units with switch & remot controler including each unit points fed through pvc insulated copper conductor sizes of 3x2.5mm2 inside PVC conduits of 16mm. diameter with all the required mounting and fitting accessories; with the following capacity of:- Capacity (air conditioner): Indoor 12000 Btu/h & Power (watt): ~2,460 watt, 220-240 Vac, 50 hz. Air switch capacity: 16A, 1ph. Operating temprature range: -5 oc - +50 oc (for cooling & heating unit).
Features of Outdoor Unit Specification
Cooling Capacity 12,000 BTU
Heating Capacity Up to 24,000 BTU
Compressor Inverter Rotary
Refrigerant R-410A
Max Connectable Capacity 12,000 BTU
Power Supply 208/230V, 1Ph, 60Hz
Noise Level ~55 dB(A)
Dimensions (W×D×H) 34.25" × 12.6" × 31.8"
Weight 130 lbs(optional)
Energy Efficiency High SEER, inverter tech
Features of Indoor Units (2 Units – Wall-Mounted) Specification
Cooling Capacity: 6,000 BTU per unit
Noise Level: As low as 19 dB(A)
Air Filtration: Multi-stage filters (dust, pollen, odors)
Smart Features: Wi-Fi control, app integration
Design: Slim profile, hidden display, quiet operation
Installation: Quick-mount system, flexible piping
Special Features
Volt Care : Protects against voltage fluctuations
Coating: Corrosion-resistant heat exchanger
GEN Mode: Operates at lower power levels for generator compatibility
Room-by-Room Control: Independent temperature settings for each zone
Controls: Central VRF controller + individual room controllers; BMS/Modbus gateway optional.
Power: Dedicated supply to outdoor; control/power to BS box and indoors per manufacturer.
Condensate: Gravity drain or pumps per unit to nearest drain points.
10.5 | A 9,000 BTU split type air conditioner system with one outdoor unit and one indoor units (Indoor-Outdoor cool & heat units) - The unit shall comply with industry, ISO/IEC standards & recommendations://for Library,EOC+Audio,PHEOC// | pc | 3 |  | 0
Supply, mount/fix, install and test wall mounted multi-split type (indoor-outdoor unit) thermally & electrically operated automated AC /cool & heat/ units with switch & remot controler including each unit points fed through pvc insulated copper conductor sizes of 3x2.5mm2 inside PVC conduits of 16mm. diameter with all the required mounting and fitting accessories; with the following capacity of:- Capacity (air conditioner): Indoor 8000 Btu/h & Power (watt): ~2,460 watt, 220-240 Vac, 50 hz. Air switch capacity: 16A, 1ph. Operating temprature range: -5 oc - +50 oc (for cooling & heating unit).
Parameter Specification
Cooling/Heating Capacity 9,000 BTU/h
Power Consumption ~2,460 W,220–240 V AC, 50 Hz
Compressor Type Inverter rotary or scroll, hermetically sealed
Refrigerant R-32 or R-410A (non-ozone depleting)
Energy Efficiency SEER ≥ 20 (Seasonal Energy Efficiency Ratio)
Air Switch Rating 16 A, 1 Phase
Operating Temperature Range -5°C to +50°C
Airflow Rate ≥ 400 CFM
Noise Level Indoor ≤ 35 dB, ≤ 50 dB
Control Infrared remote with LCD display, optional WiFi/app control
Filters Washable anti-bacterial, dust, and deodorizing filters
Casing : re-retardant ABS (indoor), galvanized steel with anti-corrosion coating (outdoor)
Standards & Compliance
ISO 15042:2017 – Performance testing and rating for multi-split systems
ISO 5151 – Non-ducted air conditioners and heat pumps
IEC 60335-2-40 – Electrical safety for AC units
Energy Efficiency: SEER ≥ 20 (where applicable)
Special Features
Volt Care : Protects against voltage fluctuations
Coating: Corrosion-resistant heat exchanger
GEN Mode: Operates at lower power levels for generator compatibility
Room-by-Room Control: Independent temperature settings for each zone
11 | Extract fan (Wall or window mount): HV-300A |  |  |  | 0
| Automatic mode operated via control unit, CR, five position 2 speed and reversible operation, class II insulation, single phase motor 230vac 50hz, 1150 rpm, automatic and thermally actuated, max absorbed power 68w, max absorbed current 0.3A, sound pressure level dBA in 3mt: with high speed 46dBA, with low speed 38dBA. Air flow rate (m3/h): high speed extraction 1100m3/h, low speed extraction 750m3/h, intake 700m3/h. Extract and supply mode: reversible. Neon lights indicating at the mode of operation. | Set | 10 |  | 0
12 | KITCHEN-HOODS: 640m3/h: HA-900N (90cm wide) |  |  |  | 0
| Air flow at free discharge 640m3/h, discharge tube diameter 120/150mm, number of motor 1, number of speed 3, sound pressure level 65dBA, voltage 230vac, power 155w, current 0.7A. | Set | 2 |  | 0
13 | PASSENGER LIFT: - (Supply, Install/assemble, Test and Commission)
| Pasangers and goods Lift of G/service standard or approved equivalent type with industry requirements and capacity of 1200kg, 13 persons, 13 stop (10 floors), speed 1.6mt/sec, stainless steel car and door, gear-less drive, etc. (Refer technical details). | Set | 2 |  | 0
General description
Type: Electric traction, machine-room- type (MR) passenger lift
Service: Passenger transport from 2 basement levels to 10 upper floors plus ground
Stops: 13 stops (B2, B1, G, 1–10)
Installation: Inside an existing reinforced concrete shaft, 2250 mm (width) × 2800 mm (depth)
Compliance: EN 81 / IS / ASME
Duty, capacity and performance
Rated load: 1200 kg (approx. 13 persons)
Rated speed: 1.6m/s
Safety: ARD, governor, overload, IR door sensor
Car dimensions and arrangement
Car type: Passenger, front entrance only
Car size:Width: 1100–1200 mm , Depth: 2100–2200 mm, Clear car height: 2200–2300 mm
Entrances: 1 front entrance at each landing
Door specifications
Door type: Automatic, centre-opening, telescopic optional if needed for space
Door clear opening width: 900–1000 mm
Door height: 2000–2100 mm clear
Door operation:
Variable-speed, frequency-controlled door operator
Adjustable open/close times
Reopening by infrared curtain/light screen
Shaft and pit
Shaft internal dimensions: 2250 mm (W) × 2800 mm (D),
Pit depth: Typically 1400–1600 mm (to be confirmed with manufacturer)
Headroom: Typically 4200–4500 mm above top landing floor level
Guide rails: Steel T‑rails for car and counterweight, fixed to shaft walls with brackets
Drive system and machine
Drive type: Gearless traction, MR
Motor:
Permanent magnet synchronous motor
Variable voltage variable frequency (VVVF) drive
Energy efficient, low noise and vibration
Drive controller: Microprocessor based, fully collective, selective control
Control and operation
a.Control type:
Collective selective, simplex (one lift)
Full collective up/down for all landings
b.Operation:
Automatic, push‑button control
Car and landing call registration with memory
Landing operating panels:
Illuminated call buttons with direction arrows
Position indicator at main entrance; optional at all landings
Car operating panel (COP):
Floor selection buttons (B2 to 10)
Door open/close, emergency stop (if permitted by code), alarm button
Digital floor position indicator and direction arrows
Overload indicator and buzzer
Emergency communication:
Two‑way intercom or auto‑dial telephone from car to building security or monitoring centre
Control System
Controller: Microprocessor-based
Operation: Collective selective
Buttons: Braille-marked, backlit
Indicators: Digital floor position & direction
Call Registration: Visual & audible acknowledgement
Safety Features (Mandatory for Hospital standard Lifts)
✔ Automatic Rescue Device (ARD)
✔ Over-speed governor
✔ Safety gear (instantaneous / progressive)
✔ Emergency alarm & intercom
✔ Battery-backed emergency light & fan
✔ Load sensor with overload alarm
Noise & Comfort
Noise Level: ≤ 60 dB in car
Smooth Acceleration / Deceleration
No jerks (patient comfort critical)
Certification requirement:
CE Marking
Factory test certificate
Installation and commissioning certificate
Safety inspection report
14 | PASSENGER & GOODS LIFT: - (Supply, Install/assemble, Test and Commission)
| Pasangers and goods Lift of G/service standard or approved equivalent type with industry requirements and capacity of 1200kg, 12 persons, 7 stop (4 floors), speed 1mt/sec, stainless steel car and door, gear-less drive, etc. (Refer technical details). | Set | 1 |  | 0
General description
Type: Electric traction, machine-room- type (MR) passenger lift
Service: Passenger transport from 2 basement levels to 10 upper floors plus ground
Stops: 7 stops (B2, B1, G, 1–4)
Installation: Inside an existing reinforced concrete shaft, 2250 mm (width) × 2800 mm (depth)
Compliance: EN 81 / IS / ASME
Stops: 7
Door Operation: Automatic, center-opening or telescopic sliding
Door Width: 900–1000 mm clear opening
Car Entrance: Single front entrance at each landing
Safety: ARD, governor, overload, IR door sensor
Compliance: EN 81 / IS / ASME
Duty, capacity and performance
Rated load: 1200 kg (approx. 13 persons)
Rated speed: 1.6m/s
Safety: ARD, governor, overload, IR door sensor
Car dimensions and arrangement
Car type: Passenger, front entrance only
Car size:Width: 1100–1200 mm , Depth: 2100–2200 mm, Clear car height: 2200–2300 mm
Entrances: 1 front entrance at each landing
Door specifications
Door type: Automatic, centre-opening, telescopic optional if needed for space
Door clear opening width: 900–1000 mm
Door height: 2000–2100 mm clear
Door operation:
Variable-speed, frequency-controlled door operator
Adjustable open/close times
Reopening by infrared curtain/light screen
Shaft and pit
Shaft internal dimensions: 2250 mm (W) × 2800 mm (D), clear
Pit depth: Typically 1400–1600 mm (to be confirmed with manufacturer)
Headroom: Typically 4200–4500 mm above top landing floor level
Guide rails: Steel T‑rails for car and counterweight, fixed to shaft walls with brackets
Drive system and machine
Drive type: Gearless traction, MR
Motor:
Permanent magnet synchronous motor
Variable voltage variable frequency (VVVF) drive
Energy efficient, low noise and vibration
Drive controller: Microprocessor based, fully collective, selective control
Control and operation
a.Control type:
Collective selective, simplex (one lift)
Full collective up/down for all landings
b.Operation:
Automatic, push‑button control
Car and landing call registration with memory
Landing operating panels:
Illuminated call buttons with direction arrows
Position indicator at main entrance; optional at all landings
Car operating panel (COP):
Floor selection buttons (B2 to 10)
Door open/close, emergency stop (if permitted by code), alarm button
Digital floor position indicator and direction arrows
Overload indicator and buzzer
Emergency communication:
Two‑way intercom or auto‑dial telephone from car to building security or monitoring centre
Control System
Controller: Microprocessor-based
Operation: Collective selective
Buttons: Braille-marked, backlit
Indicators: Digital floor position & direction
Call Registration: Visual & audible acknowledgement
Safety Features (Mandatory for Hospital standard Lifts)
✔ Automatic Rescue Device (ARD)
✔ Over-speed governor
✔ Safety gear (instantaneous / progressive)
✔ Emergency alarm & intercom
✔ Battery-backed emergency light & fan
✔ Load sensor with overload alarm
Noise & Comfort
Noise Level: ≤ 60 dB in car
Smooth Acceleration / Deceleration
No jerks (patient comfort critical)
Certification requirement:
CE Marking
Factory test certificate
Installation and commissioning certificate
Safety inspection report
| Total Sum |  |  |  | 0

## site work
Item No | Description | Unit | Qty | Rate | Amount
2.0 SITE WORK & LANDESCAPING
2.01 | Bulk excavations for ordinary soil to an average depth of 1000mm. | m³ | 2250 |  | 0
0
| Cut and Borrow to fill |  |  |  | 0
2.02 | Cut to fill/embankment, compaction to 95 % AASHTO T-180 | m³ | 795 |  | 0
2.03 | Borrow to fill, compaction to 95 % AASHTO T-181 | m³ | 1124 |  | 0
2.04 | Cut to Spoil obtained from common (normal) Excavation | m³ | 255 |  | 0
2.05 | 60cm thick Selected material fill (CBR>5) compaction to 95 % AASHTO T-180 | m³ | 1200 |  | 0
2.06 | Sub Base course (CBR>55%, PI<12%, MPD>95%, yd >1.9kg/cm’) under subbase course. The filling shall be performed in layers of 200mm with watering and consolidating each layer properly with 15-20 ton vibrating roller. | m³ | 720 |  | 0
2.07 | Base course material type one(GB1) base course (CBR>95%, PI<6%, MPD>95%, yd >2.1kg/cm’) under subbase course. The filling shall be performed in layers of 200mm with watering and consolidating each layer properly with 15-20 ton vibrating roller. | m³ | 720 |  | 0
| Concrete Pipe culvert |  |  |  | 0
2.08 | Reinforced concrete pipe On Class C-25 bedding Diameter 40 cm as per drawing. Price includes reinforcement bar, moulds, bedding materials and all unstated works. | ml | 145 |  | 0
| Concrete curbing |  |  |  | 0
2.09 | Concrete curbing, class C-20 (40cm x12cm ) as shown in the drawing. Price shall include form work,reinforcement bar,earth works, C-10 lean concrete and all related works. | ml | 285 |  | 0
2.1 | Load and cart away all excavated material to a suitable tip at a minimum distance not more than 10 km from the site. | m³ | 1994 |  | 0
Asphalt Work
2.11 | Supply and apply Prime Coat MC-30 Cut Back Asphalt (application rate 1 liter per sq.m.) | lit | 695 |  | 0
2.12 | Dense graded Asphalt AC in Wearing Course, 50mm Nominated Compacted Layer Thickness, 19mm Nominal aggregate Size with Class 60/70pen. Bitumen[Nominal Binder Content (6%)] including Supply and applying Tack Coat Grade 30 Bituminous Emulsion | m2 | 2400 |  | 0
| SITE SEWERAGE PIPES |  |  |  | 0
2.13 | Supply,lay and connect diameters indicated below uPVC PN - 6 pipe for waste water drainage system with the working pressure of 6 bars and complete with all the necessary accessories as indicated on the drawings. The pipe should laid on a red ash which have a 150mm thickness. back fill shall be well compacted in a manner that will not affect the pipe. Unit price shall include trench excavation of 80cm average depth, backfill, all assistance civil works and necessary fittings such as T, bends etc. according to where shown on the drawing |  |  |  | 0
| a) Diameter 160mm | ml | 255 |  | 0
| Manholes |  |  |  | 0
2.14 | Construct 1200mm Net Depth cast in-siut concrete manholes on main sewer, all in accordance with details shown on the drawings (type B).include for provision and fixing of cast iron steps and heavy duty tiangular mild steel frame installation of cast iron covers as detailed. Price should be inclusive of excavation,compaction,surplus material removal,installation of two flexable joints adjacent to manholes as detailed and provision of box out and sealing for all pipes and cast iron manhole cover. | No | 24 |  | 0
2.15 | Ditto but depth 1.5m-2.0m | No | 12 |  | 0
2.16 | Ditto but depth 2.0m-2.5m | No | 10 |  | 0
| ROAD CROSSING |  |  |  | 0
2.17 | Pipe encasing with 15cm thick reinforced concrete (class C-20) at main road crossing and on points with pipes having less than minimum cover for major laterals and trunk lines all around the pipe.Price shall include diameter 10mm re-bar lateral & horizontal @ 15cm spacing. | ml | 255 |  | 0
2.18 | Construct half open ditch (40 cm dia.) as per the detail drawing. Price shall include excavation, cart away and all civil assistance works and grill cover with dia. 14mm rebar with 50mm spacing flat frames and all other necessary accessories. | ml | 210 |  | 0
2.19 | Construct trapezoidal open ditch out of basaltic stone bedded in 1:3 cement sand mortar with 100cm top and 50cm bottom width and average depth 80cm. Price shall include plastering of internal surface and grill cover with dia. 14cm rebar with 50mm spacing. | ml | 42 |  | 0
2.2 | Paint ( retro-reflective road marking ) |  |  |  | 0
| (a) White lines (broken or unbroken) (100mm) | M2 | 116 |  | 0
| (b) Yellow lines (broken or unbroken) (100mm) | M2 | 116 |  | 0
| LANDSCAPING & GREENERY WORKS |  |  |  | 0
2.21 | Site clearing cutting bushes,pulling up roots and removing the top thick soil | m2 | 650 |  | 0
2.22 | Make ready for plantation by leveling the ground | m2 | 650 |  | 0
2.23 | To Supply and spread top soil with 30cm thickness | m2 | 650 |  | 0
2.24 | To Supply and spread decomposed farm yard manure for grass,lawn,shrubs and tree. | m2 | 650 |  | 0
2.25 | supply and instal decoretive clkinker stone cladding | m2 | 42 |  | 0
2.26 | Precast concrete in C-20, height 30cm, 10cm thick curb stone with 5cm bedding | ml | 122 |  | 0
2.27 | Supply and plant nursary grown flowers including verbena,geranium,snap dragon | m2 | 155 |  | 0
2.28 | Supply and instal concrete pavment of 100*100*10cm on levelled surface. | Pcs | 210 |  | 0
2.29 | Supply and plant nursary grown kikuyu grass | m2 | 460 |  | 0
2.3 | Supply and plant nursary grown climbers or golden shawer, variety | pcs | 65 |  | 0
2.31 | Supply and plant nursary grown climbers and begonvilia, begonia flowers of mixed type | pcs | 65 |  | 0
2.32 | Supply and plant nursary grown green shurbe | pcs | 40 |  | 0
2.33 | Supply and plant fiber glass made at asize of height 100cm | pcs | 165 |  | 0
2.34 | Supply and plant out door plants for fiber glass made pots | pcs | 55 |  | 0
2.35 | Supply and instal Brick masonary seatting of 45cm high | m3 | 15 |  | 0
2.36 | Supply and instal garden light point | pcs | 40 |  | 0
2.37 | General landscape design development,preparation and presntation with site supervision | lump sum | 1 |  | 0
2.38 | Gravel bedding coarse and fine aggrigate | m3 | 40 |  | 0
2.39 | Wire mesh with structure for climbers | pcs | 40 |  | 0
2.4 | Supply and apply a 4mm thick resin industrial-grade epoxy floor coating for PARKING area, including any necessary aggregate for slip resistance and Application of an approved epoxy primer to the prepared concrete surface; price shall include seal expansion joints with appropriate flexible sealant & surface preparation (Polishing Concret Suface) & make convinient for epoxy application | m2 | 1200 |  | 0
2.41 | Supply and fix Vechicle Stoppers rubber reflective anti-corruption water-resistant for parking as per detail drawing and engineer approval. | Pcs | 100 |  | 0
2.42 | Supply and fix Speed Limit class RA1 reflective face on 3mm anodised aluminum plate backing as per BS EN 12899-1:2007 as per detail drawing and engineer approval. | Pcs | 4 |  | 0
2.43 | Supply and fix Stop post-mounting class RA1 aluminum extra tough as per BS EN 12899-1:2007 as per detail drawing and engineer approval. | Pcs | 4 |  | 0
2.44 | Supply and fix Please Drive With Care 3mm plastic fitted 2 channels easy post mounting with 2x76mm clips or screwbands and universal fixing clamps as per BS EN 12899-1:2007 as per detail drawing and engineer approval. | Pcs | 2 |  | 0
2.45 | Supply and fix parking Safety Building corner protection car parking garage square rubber corner wall guard protectorwith safety reflectives. Price shall include all necessary activities to complete the work. | Pcs | 115 |  | 0
2.46 | Application of Safety Reflective paint for the wall & Columns in the parking space marking (numbers/letters), including surface cleaning and preparation, measured as the total painted area in square meters. Paint type & reflectivity shall be convienet for the parking lots & befor applying it is required the Enginners Approval | m2 | 120 |  | 0
2.47 | Supply and fix Outdoor/Indoor convex safety mirror for parking lot applications. Round, 800mm diameter, Shatter-resistant Acrylic (PMMA) lens, Weather-resistant ABS Plastic backing, Safety Orange frame. Fully weatherproof and UV resistant. Complete with heavy-duty galvanized steel pole mounting bracket (for 48-76mm dia. poles) allowing multi-angle adjustment.Price shall include all the necessary materials that complete the work. | Pcs | 3 |  | 0
2.48 | OFFICE LABELING- Backplate: Golden imitation plexi-glass Font/Graphic: Black engraving Size: 40 x 20 cm -Recessed character Price shall includes decorative stainless steel round standoff anchor type fittings and all necessary accessories. | Pcs | 95 |  | 0
| TOTAL CARRIED TO SUMMARY ..................................... |  |  |  | 0